Series

OTP-O	Olympia Ductless Single Zone Heat Pump

Features

Operation mode	- 	Cooling, heating, dehumidifying, fan and auto.

Nominal capacity	-	9000, 12000, 18000, 24000 BTU/hr.

Voltage	-	230/208V, 60 Hz, 1-phase.

Indoor unit	- 	High wall installation, dual side connection.

-	Plastic housing, standard white.

-	7-speed cross-flow fan (turbo, high, medium-high, medium, medium-low, low and quiet).

-	Washable filters.

Outdoor unit	-	Variable speed rotary compressor (INVERTER), with overload protection.

-	Electronic expansion valve for precise control of refrigerant flow.

-	Condenser fins covered with a hydrophilic coating for improved corrosion resistance.

-	Large diameter quiet axial-flow fan for more efficient heat exchange.

-	Smart pan heater to prevent ice formation.

-	Compressor blanket and preheating technology.

-		Installation on aluminum wall bracket or ground stand (optional).

Connection piping	-	Minimum piping length of 10 ft. (3 m).

- Flared connections.

Control 	-	Wireless remote included.

- 	Wired wall controller available.

-	Wi-Fi capability.
-	Interface (options HP6000ZB-GE and GT130 required).

-	Set temperature: 16 to 30 °C (61 to 86 °F).

-	Temperature display format °C or °F.

Warranty	-	10-year basic warranty on parts and 10-year basic warranty on the compressor (labour not included).

Application	-	Dining room-kitchen, living room, family room, commercial building, office building, condo, 
restaurant.

Models

| Product #1 | Indoor Unit | UHD09KCH38SB-I | UHD12KCH31S-I | UHD18KCH25S-I | UHD24KCH22S-I |
| --- | --- | --- | --- | --- | --- |
|  | Outdoor Unit | UHD09KCH38SB-O | UHD12KCH31S-O | UHD18KCH25S-O | UHD24KCH22S-O |
| Qty |  |  |  |  |
| Technical Performance |
| Voltage |  | Volts | 230/208 | 230/208 | 230/208 | 230/208 |
| Cooling capacity | Nominal | W (BTU/hr) | 2638 (9000) | 3517 (12000) | 5276 (18000) | 6450 (22000) |
|  | Min. – max. | W (BTU/hr) | 450 - 3800 (1535 - 12966) | 850 - 4500 (2900 - 15354) | 1200 - 6400 (4094 - 21837) | 2000 - 9000 (6800 - 30700) |
| Heating capacity | Nominal | W (BTU/hr) | 2638 (9000) | 3575 (12200) | 5276 (18000) | 7000 (24000) |
|  | Min. – max. | W (BTU/hr) | 700 - 4000 (2388 - 13648) | 900 - 5500 (3071 - 18766) | 1200 - 7200 (4094 - 24566) | 2000 - 9500 (6800 - 32000) |
| Used cooling power input | Nominal | W | 540 | 785 | 1330 | 1700 |
|  | Min. – max. | W | 50 - 1400 | 75 - 1500 | 350 - 2500 | 450 - 3700 |
| Used heating power input | Nominal | W | 590 | 940 | 1500 | 2000 |
|  | Min. – max. | W | 200-1500 | 250 - 1600 | 350 - 2500 | 380 - 3700 |
| Used rated input | W | 1500 | 1600 | 2500 | 3700 |
| Rated current | A | 6.2 | 6.5 | 10.8 | 16.4 |
| MCA | A | 9 | 9 | 22 | 22 |
| Max. over-current protection (MOCP) | A | 15 | 15 | 30 | 35 |
| SEER | - | 38 | 30.5 | 24.5 | 21.5 |
| HSPF | - | 15 | 14 | 12 | 12 |
| EER | W/W | 4.84 | 4.48 | 3.97 | 3.81 |
| COP | W/W | 4.47 | 3.8 | 3.52 | 3.5 |
| AHRI number | - | 202110483 | 202110484 | 202110485 | 202132789 |
| ENERGY STAR | - | ( | ( | ( | ( |
| Indoor Unit |  |  |  |  |
| Dehumidification | pt/hr (l/hr) | 1.69 (0.80) | 2.96 (1.40) | 3.80 (1.80) | 5.20 (2.50) |
| Air flow volume | T / H / MH / M / ML / L / Q2 | cfm | 424 / 383 / 353 / 324 / 294 / 265 / 206 | 500 / 471 / 441 / 353 / 324 / 265 / 235 | 736 / 677 / 618 / 559 / 500 / 457 / 353 | 824 / 765 / 706 / 647 / 589 / 500 / 383 |
| Sound level | T / H / MH / M / ML / L / Q2 | dB (A) | 43 / 40 / 38 / 36 / 33 / 31 / 19 | 49 / 46 / 43 / 40 / 37 / 34 / 22 | 51 / 48 / 45 / 42 / 39 / 36 / 34 | 52 / 49 / 46 / 43 / 40 / 37 / 34 |
| Fan motor power output | W | 60 | 60 | 60 | 70 |
| Fan motor RLA | A | 0.09 | 0.09 | 0.24 | 0.38 |
| Deflector stepper motor power output | W | 2.5 / 1.5 | 2.5 / 1.5 | 2.5 / 1.5 | 2.5 |
| Net weight | lb (kg) | 29.8 (13.5) | 29.8 (13.5) | 36.4 (16.5) | 36.4 (16.5) |
| Outdoor Unit |  |  |  |  |
| Air flow volume | cfm | 2400 | 2400 | 2354 | 4000 |
| Sound level | dB (A) | 53 | 53 | 59 | 59 |
| Compressor power input | W | 1070 | 1070 | 2443 | 2443 |
| Compressor LRA | A | 35 | 35 | 30 | 30 |
| Compressor RLA | A | 6.9 | 6.9 | 15.5 | 16 |
| Fan motor power output | W | 30 | 30 | 90 | 90 |
| Fan motor RLA | A | 0.24 | 0.24 | 0.65 | 0.65 |
| Refrigerant volume (R410A) | oz (g) | 45.9 (1301) | 49.4 (1400) | 70.6 (2101) | 81.1 (2299) |
| Net weight | lb (kg) | 99.2 (45) | 99.2 (45) | 141.1 (64) | 147.7 (67) |
| Operating ambient temperature | Cooling | °C (°F) | -18 to 54 (0 to 129) |
|  | Heating | °C (°F) | -30 to 24 (-22 to 75) |
| Connection Piping/Refrigerant |
| Pre-charge length | ft. (m) | 25 (7.5) | 25 (7.5) | 25 (7.5) | 25 (7.5) |
| Additional refrigerant charge | oz/ft. (g/m) | 0.2 (20) | 0.2 (20) | 0.5 (505) | 0.5 (50) |
| Liquid pipe outer diameter | in. | 1/4 | 1/4 | 1/4 | 1/4 |
| Gas pipe outer diameter | in. | 1/2 | 1/2 | 5/8 | 5/8 |
| Maximum height difference | ft. (m) | 49 (15) | 49 (15) | 66 (20) | 98 (30) |
| Maximum total length | ft. (m) | 98 (30) | 98 (30) | 100 (30) | 164 (50) |

1 1 indoor unit and 1 outdoor unit. Note that each unit is individually packaged.

2 Cross-Flow Fan Speeds: (T) Turbo / (H) High / (MH) Medium-High / (M) Medium / (ML) Medium-Low / (L) Low / (Q) Quiet.

Capacity Variation Ratio According to Temperature

UHD09

UHD12

UHD18 & UHD24

| Indoor Unit | L | H | D | A | B | C |
| --- | --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| UHD09KCH38SB-I UHD12KCH31S-I | 39 3/16 | 970 | 11 7/8 | 302 | 8 7/8 | 225 | 4 5/8 | 117 | 27 | 685 | 7 5/8 | 194 |
| UHD18KCH25S-I UHD24KCH22S-I | 43 3/8 | 1078 | 12 7/8 | 325 | 9 13/16 | 246 | 8 9/16 | 217 | 26 15/16 | 684 | 7 7/8 | 199 |

| Outdoor Unit | L | H | D | A | B |
| --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| UHD09KCH38SB-O | 35 3/8 | 899 | 23 1/2 | 596 | 14 7/8 | 378 | 21 11/16 | 550 | 13 1/2 | 343 |
| UHD12KCH31S-O |  |  |  |  |  |  |  |  |  |  |
| UHD18KCH25S-O | 38 5/8 | 1000 | 31 1/8 | 790 | 16 13/16 | 427 | 24 | 610 | 15 9/16 | 395 |
| UHD24KCH22S-O |  |  |  |  |  |  |  |  |  |  |

Options
See OTP Options section

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrical Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact at Ouellet: |  |
| Comments: |