Series

OTP-B	Boreal Ductless Single Zone Heat Pump

22 to 18 SEER

Features

Operating mode	- 	Cooling and heating.

Nominal capacity	-	9000 BTU/hr.

Voltage	-	240/208V, 60 Hz, 1-phase.

Indoor unit	- 	High wall installation, dual side connection.

-	Plastic housing, standard white.

-	4-speed cross-flow fan (turbo, high, medium and low).

-	Smart preheating.

-	Washable filters.

Outdoor unit	-	Variable speed rotary compressor (INVERTER), with overload protection.

-	Electronic expansion valve for precise control of refrigerant flow.

-	Condenser fins covered in a blue hydrophilic coating for improved corrosion resistance.

-	Large diameter quiet axial-flow fan for more efficient heat exchange.

-	Drip pan heating cable.

-	Compressor blanket and preheating technology.

-	Cooling mode operating ambient temperature: -17 to 43 °C (0.4 to 109.4 °F).

-	Heating mode operating ambient temperature: -20 to 24 °C (-5 to 75.2 °F).

-	Installation on epoxy/polyester powder coated adjustable steel wall bracket (optional).

Refrigerant	- 	R410A refrigerant, pre-charged for 25 ft. (7.6 m) long connection piping.

Connection piping	-	Minimum piping length of 10 ft. (3 m).

- Flared connections.

Control 	-	Wireless remote included.

-	I FEEL regulation mode.

-	Set temperature: 16 to 30 °C (61 to 86 °F).

-	Modes: AUTO, COOL, DRY, FAN and HEAT.

-	SLEEP mode.

-	Timer.

-	Auto-Clean function (X-Fan).

-	Horizontal deflector adjustment.

-	Temperature display format (°C or °F).

-	Smart defrosting, starts only when required.

-	Auto restart in case of power shortage.

Warranty	Note: All heat pump systems must be installed and registered by a certified Ouellet installer to be covered by the basic warranty.

- 5-year basic warranty on parts (labour not included).

Sold separately:

- Extended warranty from the 1st to 5th year, parts and labour.

- Extended warranty from the 1st to 10th year, parts and labour with system replacement 
if the compressor fails.

Application	-	Dining room-kitchen, living room, family room, commercial building, office building, condo, restaurant.

Models

| Product #1 | OTP-B09000D-I OTP-B09000D-E |
| --- | --- |
| Qty |  |
| Technical Performance |
| Voltage |  | Volts | 240/208 |
| Cooling capacity | Nominal | W (BTU/hr) | 2637 (9000) |
|  | Min. – max. | W (BTU/hr) | 1026 - 2813 (3500 - 9600) |
| Heating capacity | Nominal | W (BTU/hr) | 2872 (9800) |
|  | Min. – max. | W (BTU/hr) | 645 - 3224 (2200 - 11000) |
| Used cooling power input | Nominal | W | 620 |
|  | Min. – max. | W | 370 – 1075 |
| Used heating power input | Nominal | W | 750 |
|  | Min. – max. | W | 200 – 900 |
| Used rated input | W | 1430 |
| Rated current | A | 7 |
| MCA | A | 15 |
| Max. over-current protection (MOCP) | A | 20 |
| SEER | - | 22 |
| HSPF | - | 9.2 |
| EER | (BTU/hr)/W | 14.2 |
| COP | (BTU/hr)/W | 14 |
| Energy Star | - | ( |
| Indoor Unit |  |
| Dehumidification | pt/hr (l/hr) | 2.54 (1.2) |
| Air flow volume | T / H / M / L2 | cfm | 306 / 277 / 253 / 218 |
| Sound level | T / H / M / L2 | dB (A) | 42 / 38 / 35 / 32 |
| Fan motor power output | W | 20 |
| Fan motor RLA | A | 0.2 |
| Deflector stepper motor power output | W | 2 |
| Weight | lb (kg) | 22 (10) |
| Outdoor Unit |  |
| Air flow volume | cfm | 941.6 |
| Sound level | dB (A) | 50 |
| Compressor manufacturer | - |
| Compressor power output | W | 860 |
| Compressor LRA | A | - |
| Compressor RLA | A | 3.2 |
| Fan motor power output | W | 30 |
| Fan motor RLA | A | 0.13 |
| Refrigerant volume (R410A) | oz (g) | 45.864 (1300) |
| Weight | lb (kg) | 79 (36) |
| Connection Piping/Refrigerant |
| Pre-charge length | ft. (m) | 25 (7.5) |
| Additional refrigerant charge | oz/ft. (g/m) | 0.2 (18.6) |
| Liquid pipe outer diameter | in. | 1/4 |
| Gas pipe outer diameter | in. | 3/8 |
| Maximum height difference | ft. (m) | 33 (10) |
| Maximum total length | ft. (m) | 50 (15.2) |
| Drain pipe inner diameter | in. | 5/8 |

1 1 indoor unit and 1 outdoor unit. Note that each unit is individually wrapped.

2 Cross-Flow Fan Speeds: (T) Turbo / (H) High / (M) Medium / (L) Low.

Options

| Product # En trousse | Description | Qty |
| --- | --- | --- |
| OTP-WB3 | Adjustable wall bracket for outdoor unit |  |
| OTP-WBRC | Wall bracket for wireless remote control |  |

| Indoor Unit | L | H | D | A | B | C |
| --- | --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| OTP-B09000D-I | 33 1/4 | 846 | 10 3/4 | 274 | 7 | 178 | 5 1/8 | 130 | 21 1/4 | 541 | 6 3/4 | 173 |

| Outdoor Unit | L | H | D | A | B |
| --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| OTP-B09000D-E | 33 3/8 | 848 | 21 1/4 | 538 | 12 5/8 | 320 | 21 1/4 | 541 | 11 1/4 | 287 |

| Adjustable Wall Bracket | L | H | D | Maximum Capacity |
| --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | lb | kg |
| OTP-WB3 | 33 1/2 | 850 | 17 3/4 | 450 | 21 11/16 | 550 | 500 | 227 |

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrical Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact at Ouellet: |  |
| Comments: |