Series

Capella 16	Ductless Single Zone Heat Pump

Features

Operation mode	-	Cooling, heating, dehumidifying, fan and auto.

Nominal capacity	-	9000, 12000, 18000, 24000 BTU/hr.

Voltage	-	230/208V, 60 Hz, 1-phase.

Indoor unit	-	High wall installation, dual side connection.

-	Plastic housing, standard white.

-	3-speed cross-flow fan (high, medium and low)

with 3 operation modes (turbo, auto and silence).

-	Evaporator fins covered with hydrophilic coating for improved corrosion resistance.

-	Washable filters.

Outdoor unit	-	Variable speed rotary compressor (INVERTER), with PCB control protection.

-	Electronic expansion valve for precise control of refrigerant flow.

- 	Condenser fins covered with a hydrophilic coating for improved corrosion resistance.

- 	Quiet axial-flow fan.

- 	Multi-hole pan with smart heater to prevent ice formation.

- 	Compressor blanket and preheating technology.

- 	Installation on aluminum wall bracket or ground stand (optional).

Connection piping	- 	Minimum piping length of 10 ft. (3 m).

- Flared connections.

Control	- 	Wireless remote included with wall bracket.

- 	Set temperature: 17 to 32 °C (63 to 90 °F).

- 	Temperature display format: °C or °F.

-	Interface (optional HP6000ZB-MA and GT130 required).

Warranty	- 	10-year basic warranty on parts and 10-year basic warranty on the compressor

(labor not included).

Application	- Dining room-kitchen, living room, family room, commercial building, office building, condo, restaurant.

Features and functions

Models

| Product #1 | Indoor Unit | 8016-C09-I | 8016-C12-I | 8016-C18-I | 8016-C24-I |
| --- | --- | --- | --- | --- | --- |
|  | Outdoor Unit | 8016-C09-O | 8016-C12-O | 8016-C18-O | 8016-C24-O |
| Qty |  |  |  |  |
| Technical Performance |
| Voltage |  | Volts | 230/208 | 230/208 | 230/208 | 230/208 |
| Cooling capacity | Nominal | W (BTU/hr) | 2639 (9000) | 3519 (12000) | 4985 (17000) | 7034 (24000) |
|  | Min. – max. | W (BTU/hr) | 0 - 3517 (0 - 12000) | 0 - 3517 (0 - 12000) | 2022 - 5744 (6900 - 19600) | 1875 - 7121 (6400 - 24300) |
| Heating capacity | Nominal | W (BTU/hr) | 3519 (12000) | 3519 (12000) | 5279 (18000) | 7038 (24000) |
|  | Min. – max. | W (BTU/hr) | 0 - 3519 (0 - 12000) | 0 - 3519 (0 - 12000) | 1314 - 5513 (4480 - 18800) | 1965 - 8064 (6700 - 27500) |
| Used cooling power input | Nominal | W | 1345 | 1385 | 1720 | 2695 |
|  | Min. – max. | W | 180 - 1180 | 180 - 1580 | 190 - 1890 | 335 - 2940 |
| Used heating power input | Nominal | W | 1180 | 1212 | 1700 | 2475 |
|  | Min. – max. | W | 350 - 1400 | 370 - 1500 | 815 - 2050 | 660 - 2600 |
| Cooling rated current | A | 5.92 | 5.92 | 7.6 | 12.3 |
| Heating rated current | A | 5.27 | 5.27 | 7.5 | 11.3 |
| MCA | A | 12 | 12 | 15 | 19 |
| Max. over-current protection (MOCP) | A | 15 | 15 | 20 | 30 |
| SEER (SEER2) | - | 16.8 (18.5) | 16.8 (17.6) | 16.8 (18.3) | 16.5 (17) |
| HSPF (HSPF2) | - | 9.4 (8.8) | 9.4 (8.8) | 9.7 (8.7) | 9.5 (8) |
| EER | W/W | 8.8 | 8.8 | 9.9 | 8.9 |
| COP | W/W | 2.9 | 2.9 | 3.1 | 2.84 |
| AHRI number | - | 207709200 | 207709201 | 207709202 | 207709203 |
| ENERGY STAR | - | - | - | - | - |
| Indoor Unit |  |  |  |  |
| Dehumidification | pt/hr (l/hr) | 2.11 (1) | 2.54 (1.2) | 3.8 (1.8) | 5.49 (2.6) |
| Air flow volume | H / M / L2 | cfm | 318 / 241 / 176 | 318 / 241 / 176 | 464 / 369/ 275 | 565 / 447 / 341 |
| Sound level | H / M / L2 | dB (A) | 41.5 / 34.5 / 25.5 | 41.5 / 34.5 / 25.5 | 44 / 38 / 30 | 46 / 40 / 33.5 |
| Fan motor power output | W | 47.4 | 47.4 | 58.5 | 89 |
| Fan motor RLA | A | 0.34 | 0.34 | 0.66 | 0.45 |
| Net weight | lb (kg) | 17.2 (7.8) | 17.2 (7.8) | 22.93 (10.4) | 28.88 (13.1) |
| Outdoor Unit |  |  |  |  |
| Air flow volume | cfm | 1058.82 | 1058.82 | 1235.29 | 1764.71 |
| Sound level | dB (A) | 54.5 | 54.5 | 57 | 59.5 |
| Compressor power input | W | 1140 | 1140 | 2085 | 2085 |
| Compressor LRA | A | - | - | - | - |
| Compressor RLA | A | 6.47 | 6.47 | 7.5 | 14.25 |
| Fan motor power output | W | - | - | - | - |
| Fan motor RLA | A | 0.34 | 0.47 | 0.82 | 0.76 |
| Refrigerant volume (R410A) | oz (g) | 25.75 (709) | 25.75 (709) | 47.97 (1332) | 62.8 (1758) |
| Net weight | lb (kg) | 52.9 (24) | 52.9 (24) | 64.15 (29.1) | 97.88 (44.4) |
| Operating ambient temperature | Cooling | °C (°F) | -20 to 50 (-4 to 122) |
|  | Heating | °C (°F) | -20 to 30 (-4 to 86) |
| Connection Piping/Refrigerant |
| Pre-charge length | ft. (m) | 25 (7.5) | 25 (7.5) | 25 (7.5) | 25 (7.5) |
| Additional refrigerant charge | oz/pi (g/m) | 0.16 (15) | 0.16 (15) | 0.16 (15) | 0.32 (30) |
| Liquid pipe outer diameter | in. | 1/4 | 1/4 | 1/4 | 3/8 |
| Gas pipe outer diameter | in. | 3/8 | 3/8 | 1/2 | 5/8 |
| Maximum height difference | ft. (m) | 33 (10) | 33 (10) | 66 (20) | 66 (20) |
| Maximum total length | ft. (m) | 82 (25) | 82 (25) | 98 (30) | 98 (30) |

1 1 indoor unit and 1 outdoor unit. Note that each unit is individually packaged.

2 Cross-Flow Fan Speeds: (H) High / (M) Medium / (L) Low.

Capacity Variation Ratio According to Temperature

| Indoor Unit | L | H | D |
| --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm |
| 8016-C09-I | 28 1/8 | 715 | 11 1/4 | 285 | 7 5/8 | 194 |
| 8016-C12-I | 31 11/16 | 805 | 11 1/4 | 285 | 7 5/8 | 194 |
| 8016-C18-I | 37 11/16 | 957 | 11 7/8 | 302 | 8 3/8 | 213 |
| 8016-C24-I | 40 15/16 | 1040 | 12 7/8 | 327 | 8 11/16 | 220 |

| Outdoor Unit | L | H | D | A | B |
| --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| 8016-C09-O 8016-C12-O | 28 3/8 | 720 | 19 1/2 | 495 | 10 5/8 | 270 | 17 13/16 | 452 | 10 1/16 | 255 |
| 8016-C18-O | 30 1/8 | 765 | 21 7/8 | 555 | 11 15/16 | 303 | 17 13/16 | 452 | 11 1/4 | 286 |
| 8016-C24-O | 35 1/16 | 890 | 26 1/2 | 673 | 13 7/16 | 342 | 26 1/8 | 663 | 13 15/16 | 354 |

Options
See OTP Options section

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrician Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact at manufacturer: |  |
| Comments: |