Series

Capella 28 Ductless Single Zone Heat Pump

Features

Operation mode	-	Cooling, heating, dehumidifying, fan and auto.

Nominal capacity	-	9000, 12000, 18000, 24000 BTU/hr.

Voltage	-	230/208V, 60 Hz, 1-phase.

Indoor unit	-	High wall installation, dual side connection.

-	Plastic housing, standard white.

-	Cross-flow fan with selectable speed from 0% to 100% and

3 operation modes (turbo, auto and silence).

-	Evaporator fins covered with hydrophilic coating for improved 	corrosion resistance.

-	Washable filters.

Outdoor unit	-	Variable speed rotary compressor (INVERTER), with PCB control protection.

-	Electronic expansion valve for precise control of refrigerant flow.

- 	Condenser fins covered with a hydrophilic coating for improved corrosion resistance.

- 	Quiet axial-flow fan.

- 	Multi-hole pan with smart heater to prevent ice formation.

- 	Compressor blanket and preheating technology.

- 	Installation on aluminum wall bracket or ground stand (optional).

Connection piping	- 	Minimum piping length of 10 ft. (3 m).

- Flared connections.

Control	- 	Wireless remote included with wall bracket.

- 	Set temperature: 16 to 32 °C (61 to 90 °F).

- 	Temperature display format: °C or °F.

-	Interface (optional HP6000ZB-MA and GT130 required).

Warranty	- 	10-year basic warranty on parts and 10-year basic warranty on the compressor (labor not included).

- 	Labour warranty (sold separately) from the 1st to 10th year, on parts and labour with system replacement if the compressor fails.

Application	- Dining room-kitchen, living room, family room, commercial building, office building, condo, restaurant.

Features and functions

Models

| Product #1 |  |  | Indoor Unit |  | 8028-C09-I | 8028-C12-I | 8028-C18-I | 8028-C24-I |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Outdoor Unit |  | 8028-C09-O | 8028-C12-O | 8028-C18-O | 8028-C24-O |
| Qty |  |  |  |  |  |  |  |  |
| Technical Performance |  |  |  |  |  |  |  |  |
| Voltage |  |  |  | Volts | 230/208 | 230/208 | 230/208 | 230/208 |
| Cooling capacity |  | Nominal |  | W (BTU/hr) | 2638 (9000) | 3517 (12000) | 5275 (18000) | 7034 (24000) |
|  |  | Min. – max. |  | W (BTU/hr) | 967 - 4191 (3300 - 14300) | 967 - 4191 (3300 - 14300) | 2600 - 5687 8870 - 19400 | 2008 - 7913 6850 - 27000 |
| Heating capacity |  | Nominal |  | W (BTU/hr) | 3460 (11800) | 3517 (12000) | 5275 (18000) | 8504 (29000) |
|  |  | Min. – max. |  | W (BTU/hr) | 1465 - 4455 (5000 - 15200) | 1465 - 4484 (5000 - 15300) | 4425 - 5715 (15100 - 19500) | 3488 - 9085 (11900 - 31000) |
| Used cooling power input |  | Nominal |  | W | 556 | 857 | 1440 | 1845 |
|  |  | Min. – max. |  | W | 180 - 1180 | 180 - 1180 | 230 - 1760 | 310 - 2400 |
| Used heating power input |  | Nominal |  | W | 907 | 907 | 1700 | 2500 |
|  |  | Min. – max. |  | W | 370 - 1500 | 370 - 1500 | 1390 - 2050 | 670 - 2700 |
| Cooling rated current |  |  |  | A | 2.5 | 3.72 | 6.3 | 8.1 |
| Heating rated current |  |  |  | A | 4.1 | 4.1 | 7.3 | 10.9 |
| MCA |  |  |  | A | 15 | 15 | 16 | 25 |
| Max. over-current protection (MOCP) |  |  |  | A | 15 | 15 | 25 | 35 |
| SEER (SEER2) |  |  |  | - | 28.1 (28.1) | 25.5 (25.5) | 21.5 (21.5) | 21.5 (21.5) |
| HSPF (HSPF2) |  |  |  | - | 13 (11.5) | 13 (10.4) | 13 (11.3) | 12 (11.4) |
| EER |  |  |  | W/W | 16.2 | 14 | 12.5 | 13 |
| COP |  |  |  | W/W | 3.81 | 3.88 | 3.1 | 3.4 |
| AHRI number |  |  |  | - | 207709204 | 207709205 | 207709206 | 207709207 |
| ENERGY STAR |  |  |  | - |  |  |  |  |
| Indoor Unit |  |  |  |  |  |  |  |  |
| Dehumidification |  |  |  | pt/hr (l/hr) | 2.13 (1.14) | 2.54 (1.44) | 3.8 (2.16) | 5.49 (3.13) |
| Air flow volume |  | H / M / L2 |  | cfm | 335 / 229 / 176 | 335 /229 / 176 | 524 / 376 / 306 | 611 / 414 / 319 |
| Sound level |  | H / M / L2 |  | dB (A) | 38 / 33.5 / 23.5 | 38 / 33.5 / 23.5 | 46 / 42 / 24 | 46 / 39 / 34 |
| Fan motor power output |  |  |  | W | 50 | 50 | 36 | 58 |
| Fan motor RLA |  |  |  | A | 0.25 | 0.25 | 0.4 | 0.5 |
| Net weight |  |  |  | lb (kg) | 22.7 (10.3) | 22.9 (10.4) | 27 (12.3) | 44 (20) |
| Outdoor Unit |  |  |  |  |  |  |  |  |
| Air flow volume |  |  |  | cfm | 1324 | 1324 | 1765 | 2235 |
| Sound level |  |  |  | dB (A) | 55 | 56 | 59 | 62 |
| Compressor power input |  |  |  | W | 885 | 885 | 2045 | 2045 |
| Compressor LRA |  |  |  | A | 8.8 | 8.8 | 14.25 | 17.1 |
| Compressor RLA |  |  |  | A | 50 | 50 | 36 | 58 |
| Fan motor power output |  |  |  | W | - | - | - | - |
| Fan motor RLA |  |  |  | A | 0.42 | 0.36 | 0.76 | 0.5 |
| Refrigerant volume (R410A) |  |  |  | oz (g) | 41.62 (1180) | 41.62 (1180) | 65.2 (1850) | 91.7 (2600) |
| Net weight |  |  |  | lb (kg) | 74 (33.6) | 74 (33.4) | 101 (45.8) | 134 (61) |
| Operating ambient temperature | Cooling |  |  | °C (°F) |  | -30 to 50 (-22 to 122) |  |  |
|  | Heating |  |  | °C (°F) |  | -30 to 30 (-22 to 86) |  |  |
| Connection Piping/Refrigerant |  |  |  |  |  |  |  |  |
| Pre-charge length |  |  |  | ft. (m) | 25 (7.5) | 25 (7.5) | 25 (7.5) | 25 (7.5) |
| Additional refrigerant charge |  |  |  | oz/ft. (g/m) | 0.16 (15) | 0.16 (15) | 0.16 (15) | 0.32 (30) |
| Liquid pipe outer diameter |  |  |  | in. | 1/4 | 1/4 | 1/4 | 3/8 |
| Gas pipe outer diameter |  |  |  | in. | 3/8 | 1/2 | 1/2 | 5/8 |
| Maximum height difference |  |  |  | ft. (m) | 33 (10) | 33 (10) | 66 (20) | 82 (25) |
| Maximum total length |  |  |  | ft. (m) | 82 (25) | 82 (25) | 98 (30) | 164 (50) |

1 1 indoor unit and 1 outdoor unit. Note that each unit is individually packaged.

2 Cross-Flow Fan Speeds: (H) High (80%) / (M) Medium (60%) / (L) Low (40%).

Capacity Variation Ratio According to Temperature

| Indoor Unit | L |  | H |  | D |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm |
| 8028-C09-I 8028-C12-I | 31 5/16 | 795 | 11 5/8 | 295 | 8 7/8 | 225 |
| 8028-C18-I | 38 | 965 | 12 9/16 | 319 | 9 7/16 | 239 |
| 8028-C24-I | 44 7/8 | 1140 | 14 9/16 | 370 | 10 13/16 | 275 |

| Outdoor Unit | L |  | H |  | D |  | A |  | B |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| 8028-C09-O 8028-C12-O | 31 11/16 | 805 | 21 13/16 | 554 | 13 | 330 | 20 1/8 | 511 | 12 | 305 |
| 8028-C18-O | 35 1/16 | 890 | 26 1/2 | 673 | 13 7/16 | 342 | 26 1/8 | 663 | 13 11/16 | 348 |
| 8028-C24-O | 37 1/4 | 946 | 31 7/8 | 810 | 16 1/8 | 410 | 26 1/2 | 673 | 17 15/16 | 455 |

Options
See OTP Options section

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrician Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact at manufacturer: |  |
| Comments: |  |