Series

Capella MZ			Ductless Multizone Heat Pump

Features

Operation mode	- 	Cooling, heating, dehumidifying, fan and auto.

Nominal capacity	-	18000, 27000, 36000, 48000 BTU/hr.

Voltage	-	230/208V, 60 Hz, 1-phase.

Indoor unit	- 	High wall installation, dual side connection.

-	Plastic housing, standard white.

-	Cross-flow fan with selectable speed from 0% to 100% and 3 operation modes (turbo, auto and silence).

-	Evaporator fins covered with hydrophilic coating for improved 	corrosion resistance.

-	Washable filters.

Outdoor unit	-	Variable speed rotary compressor (INVERTER), with PCB control protection.

-	Electronic expansion valve for precise control of refrigerant flow.

-	Condenser fins covered with a hydrophilic coating for improved corrosion resistance.

-	Quiet axial-flow fan.

-	Multi-hole pan with smart heater to prevent ice formation.

-	Compressor blanket and preheating technology.

-	Installation on adjustable wall bracket or ground stand (optional).

Connection piping	-	Minimum piping length of 10 ft. (3 m).

- Flared connections.

Control 	-	Wireless remote with wall bracket included with each indoor unit.

-	Set temperature: 16 to 32 °C (61 to 90 °F).

-	Temperature display format: °C or °F.

Warranty	-  10-year basic warranty on parts and 10-year basic warranty on the compressor 
(labour not included).

- Labour warranty (sold separately) from the 1st to 10th year, on parts and labour with system replacement if the compressor fails.

Application	-	Dining room-kitchen, living room, family room, commercial building, office building, condo, restaurant.

Features and functions

Outdoor Unit Models

| Product # |  |  |  | 8222-C18-O | 8322-C27-O | 8422-C36-O | 8522-C48-O |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Qty |  |  |  |  |  |  |  |
| Technical Performance |  |  |  |  |  |  |  |
| Number of connectable indoor unit |  |  | - | 1 to 2 | 2 to 3 | 2 to 4 | 2 to 5 |
| Voltage |  |  | Volts | 230/208 | 230/208 | 230/208 | 230/208 |
| Cooling capacity |  | Nominal | W (BTU/hr) | 5572 (19000) | 8211 (28000) | 10557 (36000) | 14076 (48000) |
|  |  | Min. – max. | W (BTU/hr) | 1613 - 1804 (5500 - 25000) | 2344 - 9626 (7995 - 32826) | 5249 - 12317 (17900 - 42000) | 5660 - 14956 (19300 - 51000) |
| Heating capacity |  | Nominal | W (BTU/hr) | 5882 (20000) | 8211 (28000) | 10704 (36500) | 14370 (49000) |
|  |  | Min. – max. | W (BTU/hr) | 2375 - 8710 (8100 - 29700) | 1477 - 10765 (5035 - 38712) | 3666 - 14370 (12500 - 49000) | 3372 - 17008 (11500 - 58000) |
| Used cooling power input |  | Nominal | W | 1520 | 2240 | 2650 | 4150 |
|  |  | Min. – max. | W | 230 - 2200 | 275 - 3493 | 740 - 4030 | 685 - 4700 |
| Used heating power input |  | Nominal | W | 1725 | 2240 | 2780 | 4000 |
|  |  | Min. – max. | W | 640 - 2700 | 303 - 4074 | 770 - 5230 | 710 - 5800 |
| MCA |  |  | A | 20 | 25 | 40 | 42 |
| Max. over-current protection (MOCP) |  |  | A | 25 | 40 | 50 | 50 |
| SEER (SEER2) |  |  | - | 22 (22) | 22.5 (23) | 21.8 (22.2) | 21.5 (21.8) |
| HSPF (HSPF2) |  |  | - | 10.2 (9.8) | 11.3 (10.6) | 11 (10.3) | 11 (9.8) |
| EER |  |  | W/W | 12.5 | 12.5 | 13.6 | 11.6 |
| COP |  |  | W/W | 3.40 | 3.66 | 3.85 | 3.59 |
| AHRI number |  |  | - | 207590846 | 207590849 | 207657622 | 207590852 |
| ENERGY STAR |  |  | - |  |  |  |  |
| Air flow volume |  |  | cfm | 2129 | 2147 | 4500 | 4500 |
| Sound level |  |  | dB (A) | 61 | 63 | 63 | 65 |
| Compressor power input |  |  | W | 1895 | 2600 | 3040 | 3565 |
| Compressor LRA |  |  | A | - | - | - | - |
| Compressor RLA |  |  | A | 18 | 20 | 26 | 30 |
| Fan motor power output |  |  | W | 150 | 150 | 126 | 126 |
| Fan motor RLA |  |  | A | - | - | - | - |
| Refrigerant volume (R410A) |  |  | oz (g) | 91.7 (2600) | 134.04 (3800) | 162 (4600) | 162 (4600) |
| Net weight |  |  | lb (kg) | 138 (63) | 168 (76) | 223 (101) | 238 (108) |
| Operating ambient temperature | Cooling |  | °C (°F) | -30 to 50 (-22 to 122) |  |  |  |
|  | Heating |  | °C (°F) | -30 to 30 (-22 to 86) |  |  |  |
| Connection Piping/Refrigerant |  |  |  |  |  |  |  |
| Pre-charge length |  |  | ft. (m) | 49 (15) | 74 (22.5) | 98 (30) | 123 (37.5) |
| Additional refrigerant charge |  |  | oz/ft. (g/m) | 0.16 (15) | 0.16 (15) | 0.16 (15) | 0.16 (15) |
| Liquid pipe outer diameter |  |  | in. | 1/4 | 1/4 | 1/4 | 1/4 |
| Gas pipe outer diameter |  |  | in. | 3/8 | 3/8 | 3/8 | 3/8 |
| Max. height difference outdoor to indoor unit |  |  | ft. (m) | 49 (15) | 49 (15) | 49 (15) | 49 (15) |
| Max. height difference between indoor units |  |  | ft. (m) | 33 (10) | 33 (10) | 33 (10) | 33 (10) |
| Max. length outdoor to last indoor unit |  |  | ft. (m) | 82 (25) | 98 (30) | 118 (35) | 115 (35) |
| Max. total length |  |  | ft. (m) | 131 (40) | 197 (60) | 262 (80) | 262 (80) |

Indoor Unit Models

| Product # |  |  |  | 8028-C09-I | 8028-C12-I | 8028-C18-I | 8028-C24-I |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Qty |  |  |  |  |  |  |  |
| Cooling capacity | Nominal |  | W (BTU/hr) | 2638 (9000) | 3517 (12000) | 5275 (18000) | 7034 (24000) |
|  | Min. – max. |  | W (BTU/hr) | 967 - 4191 (3300 - 14300) | 967 - 4191 (3300 - 14300) | 2600 - 5687 (8870 - 19400) | 2008 - 7913 (6850 - 27000) |
| Heating capacity | Nominal |  | W (BTU/hr) | 3460 (11800) | 3517 (12000) | 5275 (18000) | 8504 (29000) |
|  | Min. – max. |  | W (BTU/hr) | 1465 - 4455 (5000 - 15200) | 1465 - 4484 (5000 - 15300) | 4425 - 5715 (15100 - 19500) | 3488 - 9085 (11900 - 31000) |
| Dehumidication |  |  | pt/hr (l/hr) | 2.13 (1.14) | 2.54 (1.44) | 3.8 (2.16) | 5.49 (3.13) |
| Air flow volume |  | H / M / L1 | cfm | 335 / 229 / 176 | 335 / 229 / 176 | 524 / 376 / 306 | 611 / 414 / 319 |
| Sound level |  | H / M / L1 | dB (A) | 38 / 33.5 / 23.5 | 38 / 33.5 / 23.5 | 46 / 42 / 24 | 46 / 39 / 34 |
| Fan motor power output |  |  | W | 50 | 50 | 36 | 58 |
| Fan motor RLA |  |  | A | 0.25 | 0.25 | 0.4 | 0.5 |
| Net weight |  |  | lb (kg) | 23 (10.3) | 23 (10.4) | 27 (12.3) | 44 (20) |

1 Cross-Flow Fan Speeds: (H) High (80%) / (M) Medium (60%) / (L) Low (40%).

Note that each unit is individually packaged.

| Indoor Unit | L |  | H |  | D |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm |
| 8028-C09-I 8028-C12-I | 31 5/16 | 795 | 11 5/8 | 295 | 8 7/8 | 225 |
| 8028-C18-I | 38 | 965 | 12 9/16 | 319 | 9 7/16 | 239 |
| 8028-C24-I | 44 7/8 | 1140 | 14 9/16 | 370 | 10 13/16 | 275 |

| Outdoor Unit | L |  | H |  | D |  | A |  | B |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| 8222-C18-O 8322-C27-O | 37 1/4 | 946 | 31 7/8 | 810 | 16 1/8 | 410 | 26 1/2 | 673 | 15 7/8 | 403 |
| 8422-C36-O 8522-C48-O | 37 1/2 | 952 | 52 1/2 | 1333 | 16 5/16 | 415 | 24 15/16 | 634 | 15 15/16 | 404 |

Options
See OTP Options section

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrical Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact at manufacturer: |  |
| Comments: |  |