Series

OAS	Commercial Industrial Suspended Unit Heater

Features

Color	-	Standard: almond.

Finish	-	Standard: epoxy/polyester powder paint.

Voltage	-	208V, 240V, 277V, 347V, 480V, 600V, 1 or 3-phase.

-	Some units may be field converted from 3 to 1-phase.

Construction	-	18 and 20-gauge steel.

-	Adjustable louvres to direct air flow.

-	High-limit temperature control with automatic reset.

Fan	-		Totally enclosed factory-lubricated ball bearing motor

(except for 15 to 25kW at 208/240V).

-	58 dBA fan (2 to 10kW), 67 dBA fan (15 to 30kW) and 77 dBA fan (40 to 60kW).

- Thermally-protected motor mounted in cold compartment.

- Fan delay purges heater of residual heat.

Heating element	-	Tubular heating elements; stainless steel (2 to 10kW); finned steel (15 to 60kW).

- Concentric disposition of heating elements.

- Factory sealed element upon request.

Control	-	Factory-installed contactor and 240/208V control circuit standard 
(with transformer if necessary).

-	24V relay, with or without transformer available.

-	120V control circuit available.

- 	Built-in thermostat available.

Ouellet highly recommends to use a wall thermostat for greater comfort.

Any remote thermostat or relay must be connected to the heater control terminal block.

Installation	-		Not for residential use in the United States.

- Horizontal mounting:

2 to 30kW: wall or ceiling using the supplied brackets which allow 360° rotation.

40 to 60kW: ceiling only secured by the supplied 4 hooks of suspension.

-	Vertical mounting (except option -MD):

2 to 60kW: using 4 threaded rods 1/2 in. X 13 UNC (not included).

-	Diffuser cones available (except option -MD).

-	Maximum recommended height (horizontal): 2 to 10kW:  8 ft. (2.4 m),

15 to 30kW: 10 ft. (3 m), 40 to 60kW: 15 ft. (4.5 m).

-	Protective screen allows minimum horizontal mounting height:

Canada 2 to 30 kW: 24 in. (610 mm), 40 to 60kW: 8 ft. (2.4 m).

United States 2 to 30 kW 6 ft. (1.8 m), 40 to 60kW: 8 ft. (2.4 m).

-	30 °C (85 °F) maximum operating ambient temperature.

Warranty	-	3-year warranty against defects.

Application	-	Commercial hall, warehouse, stairwell, factory.

Models

| Product # | Qty | Volts | Phase | kW (BTU/hr) | cfm | Temperature Rise |  | Motor |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | oC | oF | HP | rpm |
| OASU05000AM-T2 |  | 240 | 1 | 5.0 (17060) | 700 | 13 | 23 | 1/30 | 1550 |
| OASU07500AM-T2 |  | 240 | 1 | 7.5 (25590) | 700 | 19 | 34 | 1/30 | 1550 |
| OASU10000AM-T2 |  | 240 | 1 | 10.0 (34120) | 700 | 25 | 45 | 1/30 | 1550 |
| OASU05034AM-T2 |  | 480 | 3 | 5.0 (17060) | 700 | 13 | 23 | 1/30 | 1550 |
| OASU07534AM-T2 |  | 480 | 3 | 7.5 (25590) | 700 | 19 | 34 | 1/30 | 1550 |
| OASU10034AM-T2 |  | 480 | 3 | 10.0 (34120) | 700 | 25 | 45 | 1/30 | 1550 |
| OASU02008 |  | 208 | 1 | 2.0 (6824) | 510 | 7 | 13 | 1/30 | 1550 |
| OASU03008 |  | 208 | 1 | 3.0 (10236) | 510 | 10 | 18 | 1/30 | 1550 |
| OASU04008 |  | 208 | 1 | 4.0 (13648) | 510 | 14 | 25 | 1/30 | 1550 |
| OASU05008 |  | 208 | 1 | 5.0 (17060) | 700 | 13 | 23 | 1/30 | 1550 |
| OASU05038 |  | 208 | 3/11 | 5.0 (17060) | 700 | 13 | 23 | 1/30 | 1550 |
| OASU07538 |  | 208 | 3/11 | 7.5 (25590) | 700 | 19 | 34 | 1/30 | 1550 |
| OASU10008 |  | 208 | 1 | 10.0 (34120) | 700 | 25 | 45 | 1/30 | 1550 |
| OASU10038 |  | 208 | 3 | 10.0 (34120) | 700 | 25 | 45 | 1/30 | 1550 |
| OASU15038 |  | 208 | 3 | 15.0 (51180) | 1300 | 20 | 36 | 1/8 | 1550 |
| OASU20038 |  | 208 | 3 | 20.0 (68240) | 1300 | 27 | 49 | 1/8 | 1550 |
| OASU25038 |  | 208 | 3 | 25.0 (85300) | 1300 | 34 | 61 | 1/8 | 1550 |
| OASU02000 |  | 240 | 1 | 2.0 (6824) | 510 | 7 | 13 | 1/30 | 1550 |
| OASU03000 |  | 240 | 1 | 3.0 (10236) | 510 | 10 | 18 | 1/30 | 1550 |
| OASU04000 |  | 240 | 1 | 4.0 (13648) | 510 | 14 | 25 | 1/30 | 1550 |
| OASU05000 |  | 240 | 1 | 5.0 (17060) | 700 | 13 | 23 | 1/30 | 1550 |
| OASU05030 |  | 240 | 3/11 | 5.0 (17060) | 700 | 13 | 23 | 1/30 | 1550 |
| OASU07500 |  | 240 | 1 | 7.5 (25590) | 700 | 19 | 34 | 1/30 | 1550 |
| OASU07530 |  | 240 | 3/11 | 7.5 (25590) | 700 | 19 | 34 | 1/30 | 1550 |
| OASU10000 |  | 240 | 1 | 10.0 (34120) | 700 | 25 | 45 | 1/30 | 1550 |
| OASU10030 |  | 240 | 3/11 | 10.0 (34120) | 700 | 25 | 45 | 1/30 | 1550 |
| OASU15030 |  | 240 | 3 | 15.0 (51180) | 1300 | 20 | 36 | 1/8 | 1550 |
| OASU20030 |  | 240 | 3 | 20.0 (68240) | 1300 | 27 | 49 | 1/8 | 1550 |
| OASU25030 |  | 240 | 3 | 25.0 (85300) | 1300 | 34 | 61 | 1/8 | 1550 |
| OASU02077 |  | 277 | 1 | 2.0 (6824) | 510 | 7 | 13 | 1/30 | 1550 |
| OASU03077 |  | 277 | 1 | 3.0 (10236) | 510 | 10 | 18 | 1/30 | 1550 |
| OASU04077 |  | 277 | 1 | 4.0 (13648) | 510 | 14 | 25 | 1/30 | 1550 |
| OASU05077 |  | 277 | 1 | 5.0 (17060) | 700 | 13 | 23 | 1/30 | 1550 |
| OASU07577 |  | 277 | 1 | 7.5 (25590) | 700 | 19 | 34 | 1/30 | 1550 |
| OASU02034 |  | 480 | 3 | 2.0 (6824) | 510 | 7 | 13 | 1/30 | 1550 |
| OASU03034 |  | 480 | 3 | 3.0 (10236) | 510 | 10 | 18 | 1/30 | 1550 |
| OASU04034 |  | 480 | 3 | 4.0 (13648) | 510 | 14 | 25 | 1/30 | 1550 |
| OASU05034 |  | 480 | 3 | 5.0 (17060) | 700 | 13 | 23 | 1/30 | 1550 |
| OASU07534 |  | 480 | 3 | 7.5 (25590) | 700 | 19 | 34 | 1/30 | 1550 |
| OASU10034 |  | 480 | 3 | 10.0 (34120) | 700 | 25 | 45 | 1/30 | 1550 |
| OASU15034 |  | 480 | 3 | 15.0 (51180) | 1400 | 19 | 34 | 1/3 | 1725 |
| OASU20034 |  | 480 | 3 | 20.0 (68240) | 1400 | 25 | 45 | 1/3 | 1725 |
| OASU25034 |  | 480 | 3 | 25.0 (85300) | 1400 | 31 | 56 | 1/3 | 1725 |
| OASU30034 |  | 480 | 3 | 30.0 (102360) | 1400 | 38 | 68 | 1/3 | 1725 |
| OASU40034 |  | 480 | 3 | 40.0 (136480) | 2000 | 35 | 63 | 3/4 | 1140 |
| OASU50034 |  | 480 | 3 | 50.0 (170600) | 2000 | 44 | 79 | 3/4 | 1140 |
| OASU60034 |  | 480 | 3 | 60.0 (204720) | 2000 | 53 | 95 | 3/4 | 1140 |

1 Models with the indication "3/1" can be field converted from 3 to 1-phase.

2 Come with built-in thermostat.

Standard color is almond.

Add-MD to suffix for special Mine Duty Feature. 600V available upon request. 240V, 3-phase and 480V, 1-phase available upon request.

Remember to change the 3 for 0 when ordering. E.g.: OASU05034 becomes OASU05004.

Options

| Product # Kit | Product # Factory installed* | Description | Qty |
| --- | --- | --- | --- |
| - | 120 | 120V control circuit |  |
| - | 3P | Triple-pole contactor |  |
| KIT-OAS-CD1AM | - | Diffuser cone, 2 to 10kW units |  |
| KIT-OAS-CD2AM | - | Diffuser cone, 15 to 30kW units |  |
| KIT-OAS-CD3AM | - | Diffuser cone, 40 to 60kW units |  |
| - | CV | Summer fan switch, with motor 240V and 277V |  |
| - | CV | Summer fan switch, with motor 480V and 600V |  |
| - | DIS403 | Disconnect switch, 40A |  |
| - | DIS803 | Disconnect switch, 80A |  |
| - | DIS1003 | Disconnect switch, 100A |  |
| - | ES1 | Factory sealed element |  |
| - | FANAM | Fan blades with almond epoxy/polyester coating |  |
| - | MD2 | Mine duty |  |
| KIT-OAS-R | R | 24V relay, without transformer |  |
| - | RCV240 | Summer fan relay 240V, remote control (switch not included) |  |
| KIT-OAS-RT | RT | 24V relay, with transformer |  |
| KIT-OAS-T | T | Thermostat |  |

* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover.

1 The option "sealed element" increases the reliability of these in humid environments. It does not completely eliminate the leakage currents of metal shealthed heating elements.

2 See features below.

3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect.

### Others

| Type | Quantity | Model et description Complementary informations | Volts | Phase | Watts | Length mm/in. | Informations Color/installation |
| --- | --- | --- | --- | --- | --- | --- | --- |

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrician Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact in Ouellet: |  |
| Comments: |  |