- Series

ODBA	Steel Draft Barrier

With bottom

fresh air inlet

- Features

Color 	-	Standard: white, almond.

-	Optional (upcharge applicable): metallic silver, bronze, metallic charcoal,

aluminum, semi-gloss black, sand.

-	Custom colors available upon request.

Finish	-	Standard: epoxy/polyester powder paint.

Voltage	-	120V, 208V, 240/208V, 277V, 347V, 600V, 50/60 Hz, 1-phase.

Construction	-	16-gauge steel front cover.

-	18-gauge satin coat steel cabinet.

-	Screw assembly for added strength.

-	Full length built-in wireway.

-	Front fresh air inlet; top warm air outlet.

- Bottom fresh air inlet available (-BAI).

-	Clean back available (-BD).

-	Linear high-limit temperature control with automatic reset. 
High altitude version available (-HA).

-	End caps included.

Heating element	-	Stainless steel tubular heating element with aluminum ﬁns.

-	Floating heating element on high-temperature nylon bushings

reducing expansion noises.

Watt density	-	Average standard watt density of 275W/ft.

-	Average low watt density of 100W/ft., 150W/ft., 200W/ft.

Control	-	Built-in thermostat available with a control knob

or tamperproof.

- Mechanical, electronic or pneumatic relays available

(installed on the right end only).

Ouellet highly recommends to use an electronic wall thermostat for greater comfort.

Installation	-	Heater must be installed at least 2 in. (51 mm) from finished floor

(for -BAI option).

-		Mounting holes spaced on 4 in. (102 mm) intervals for ease of installation.

-	Wall or floor mounted installation.

-	Variety of accessories available for wall-to-wall installation.

-	Pedestal kit available.

Warranty	-	3-year warranty against defects.

Application	-	Commercial building, office building, hospital, daycare center, private residence.

- Average Standard Watt Density Models 275W/ft.1

| Watts | Watts 240/208V2 | Product # |  |  |  |  |  |  |  |  |  | Length |  | Weight |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 120V | Qty | 208V | Qty | 240/208V | Qty | 347V | Qty | 600V | Qty | in. | mm | lb | kg |
| 500 | 500/375 | ODBA0502 |  | ODBA0508 |  | ODBA0500 |  | ODBA0507 |  | - | - | 28 7/8 | 733 | 10.5 | 4.8 |
| 750 | 750/563 | ODBA0752 |  | ODBA0758 |  | ODBA0750 |  | ODBA0757 |  | ODBA0756 |  | 38 7/8 | 987 | 12.7 | 5.8 |
| 1000 | 1000/750 | ODBA1002 |  | ODBA1008 |  | ODBA1000 |  | ODBA1007 |  | ODBA1006 |  | 49 1/8 | 1248 | 14.9 | 6.8 |
| 1250 | 1250/938 | ODBA1252 |  | ODBA1258 |  | ODBA1250 |  | ODBA1257 |  | ODBA1256 |  | 58 5/8 | 1489 | 17.0 | 7.7 |
| 1500 | 1500/1125 | ODBA1502 |  | ODBA1508 |  | ODBA1500 |  | ODBA1507 |  | ODBA1506 |  | 67 5/16 | 1710 | 18.8 | 8.5 |
| 1750 | 1750/1313 | - | - | ODBA1758 |  | ODBA1750 |  | ODBA1757 |  | ODBA1756 |  | 76 5/8 | 1947 | 20.8 | 9.4 |
| 2000 | 2000/1500 | - | - | ODBA2008 |  | ODBA2000 |  | ODBA2007 |  | ODBA2006 |  | 85 7/16 | 2170 | 22.7 | 10.3 |
| 2250 | 2250/1688 | - | - | ODBA2258 |  | ODBA2250 |  | ODBA2257 |  | ODBA2256 |  | 94 5/16 | 2395 | 24.6 | 11.2 |
| 2500 | 2500/1875 | - | - | ODBA2508 |  | ODBA2500 |  | ODBA2507 |  | ODBA2506 |  | 103 7/16 | 2627 | 26.6 | 12.1 |

- Average Low Watt Density Models

| Product #3 | Length | Weight | Average Density W/ft. | Watts | Watts 240/208V2 | 120V | Qty | 208V | Qty | 240/208V | Qty | 347V | Qty | 600V | Qty |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ODBA020X-733 | 28 7/8" (733 mm) | 11.6 lb (5.3 kg) | 100 | 200 | 200/150 |  |  |  |  |  |  | ----- | ----- | ----- | ----- |
| ODBA030X-733 |  |  | 150 | 300 | 300/225 |  |  |  |  |  |  | ----- | ----- | ----- | ----- |
| ODBA040X-7331 |  |  | 200 | 400 | 400/300 |  |  |  |  |  |  |  |  | ----- | ----- |
| ODBA030X-987 | 38 7/8" (987 mm) | 15.1 lb (6.9 kg) | 100 | 300 | 300/225 |  |  |  |  |  |  |  |  | ----- | ----- |
| ODBA045X-987 |  |  | 150 | 450 | 450/338 |  |  |  |  |  |  |  |  | ----- | ----- |
| ODBA060X-9871 |  |  | 200 | 600 | 600/450 |  |  |  |  |  |  |  |  | ----- | ----- |
| ODBA040X-1248 | 49 1/8" (1248 mm) | 18.7 lb (8.5 kg) | 100 | 400 | 400/300 |  |  |  |  |  |  |  |  | ----- | ----- |
| ODBA060X-1248 |  |  | 150 | 600 | 600/450 |  |  |  |  |  |  |  |  | ----- | ----- |
| ODBA080X-12481 |  |  | 200 | 800 | 800/600 |  |  |  |  |  |  |  |  |  |  |
| ODBA050X-1489 | 58 5/8" (1489 mm) | 22.0 lb (10.0 kg) | 100 | 500 | 500/375 |  |  |  |  |  |  |  |  | ----- | ----- |
| ODBA075X-1489 |  |  | 150 | 750 | 750/563 |  |  |  |  |  |  |  |  |  |  |
| ODBA100X-14891 |  |  | 200 | 1000 | 1000/750 |  |  |  |  |  |  |  |  |  |  |
| ODBA060X-1710 | 67 5/16" (1710 mm) | 25.0 lb (11.4 kg) | 100 | 600 | 600/450 |  |  |  |  |  |  |  |  |  |  |
| ODBA090X-1710 |  |  | 150 | 900 | 900/675 |  |  |  |  |  |  |  |  |  |  |
| ODBA120X-17101 |  |  | 200 | 1200 | 1200/900 |  |  |  |  |  |  |  |  |  |  |
| ODBA070X-1947 | 76 5/8" (1947 mm) | 28.3 lb (12.8 kg) | 100 | 700 | 700/525 |  |  |  |  |  |  |  |  |  |  |
| ODBA105X-1947 |  |  | 150 | 1050 | 1050/788 |  |  |  |  |  |  |  |  |  |  |
| ODBA140X-19471 |  |  | 200 | 1400 | 1400/1050 |  |  |  |  |  |  |  |  |  |  |
| ODBA080X-2170 | 85 7/16" (2170 mm) | 31.3 lb (14.2 kg) | 100 | 800 | 800/600 |  |  |  |  |  |  |  |  |  |  |
| ODBA120X-2170 |  |  | 150 | 1200 | 1200/900 |  |  |  |  |  |  |  |  |  |  |
| ODBA160X-21701 |  |  | 200 | 1600 | 1600/1200 |  |  |  |  |  |  |  |  |  |  |
| ODBA090X-2395 | 94 5/16" (2395 mm) | 34.4 lb (15.6 kg) | 100 | 900 | 900/675 |  |  |  |  |  |  |  |  |  |  |
| ODBA135X-2395 |  |  | 150 | 1350 | 1350/1013 | ----- | ----- |  |  |  |  |  |  |  |  |
| ODBA180X-23951 |  |  | 200 | 1800 | 1800/1350 | ----- | ----- |  |  |  |  |  |  |  |  |
| ODBA100X-2627 | 103 7/16" (2627 mm) | 37.6 lb (17.6 kg) | 100 | 1000 | 1000/750 |  |  |  |  |  |  |  |  |  |  |
| ODBA150X-2627 |  |  | 150 | 1500 | 1500/1125 | ----- | ----- |  |  |  |  |  |  |  |  |
| ODBA200X-26271 |  |  | 200 | 2000 | 2000/1500 | ----- | ----- |  |  |  |  |  |  |  |  |
| ODBA225X-26271 |  |  | 200 | 2250 | 2250/1688 | ----- | ----- |  |  |  |  |  |  |  |  |

- 1 Not for residential use in the United States.

- 2 208V = 75% of wattage at 240V.

- 3 X = 2 (120V), 8 (208V), 0 (240/208V), 7 (347V), 6 (600V).

-  = Available.

- Add "BL" for white, "AM" for almond.

Other colors, accessories and finishes are available upon request. Please contact your customer service representative.

Other voltages available upon request.

- Options

| Product # Kit | Product # Factory installed* | Description | Qty |
| --- | --- | --- | --- |
| Finish |  |  |  |
| - | BAI | Bottom fresh air inlet |  |
| - | BD | Clean back |  |
| KIT-ODBA-CE | - | Outside corner, 4 in. (102 mm) |  |
| KIT-ODBA-CI | - | Inside corner, 4 in. (102 mm) |  |
| KIT-ODBA-JT | - | Splice plate, 2 in. (51 mm) |  |
| KIT-ODBA-JT-PE | - | Contour splice plate for BD option and/or heater with pedestals, 2 in. (51 mm) |  |
| KIT-ODBA-PE | - | Round pedestal kit (2), 3 in. (76 mm) |  |
| KIT-ODBA-PEC | - | Square-shaped pedestal kit (2), 2 in. (51 mm) |  |
| ODBA-SV-XX | - | Empty cabinet length of XX mm (minimum: 154 mm, maximum: 2625 mm) |  |
| Controls |  |  |  |
| KIT-ODBA-DIS203 | DIS203 | Disconnect switch, 20A at 277V max. |  |
| KIT-ODBA-DIS403 | DIS403 | Disconnect switch, 40A at 600V max. |  |
| - | HA | Linear high-limit temperature control for high altitude (3000 ft. to 8200 ft.) |  |
| - | PM | Pneumatic relay, 20A at 600V max. |  |
| KIT-ODBA-R-347 | R | Single-pole relay, coil 24V, without transformer: 22A at 120V, 208V, 240V - 19A at 277V - 18A at 347V |  |
| KIT-ODBA-R-600 | R | Single-pole relay, coil 24V, without transformer, 10A at 600V |  |
| KIT-ODBA-RT-1201 | RT1 | Single-pole relay, coil 24V, with transformer 120V/24V, 22A at 120V |  |
| KIT-ODBA-RT-208 | RT | Single-pole relay, coil 24V, with transformer 208V/24V, 22A at 208V |  |
| KIT-ODBA-RT-240 | RT | Single-pole relay, coil 24V, with transformer 240V/24V, 22A at 240V |  |
| KIT-ODBA-RT-277 | RT | Single-pole relay, coil 24V, with transformer 277V/24V, 19A at 277V |  |
| KIT-ODBA-RT-347 | RT | Single-pole relay, coil 24V, with transformer 347V/24V, 18A at 347V |  |
| KIT-ODBA-RT-6001 | RT1 | Single-pole relay, coil 24V, with transformer 600V/24V, 10A at 600V (2-wire only) |  |
| KIT-ODBA-TB6 | TB6 | Single-pole bi-metal thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V |  |
| KIT-ODBA-TB262 | TB262 | Double-pole bi-metal thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V |  |
| KIT-ODBA-TB6-AV | TB6AV | Single-pole bi-metal tamperproof thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V |  |
| KIT-ODBA-TB26-AV2 | TB26AV2 | Double-pole bi-metal tamperproof thermostat: 25A at 120V, 208V, 240V, 277V - 10A at 347V, 480V, 600V |  |
| KIT-ODBA-TRIAC-347 | TRIAC | Single-pole electronic relay, coil 24V, without transformer, 15A max. at 347V max. |  |
| KIT-ODBA-TRIAC-347T | TRIACT | Single-pole electronic relay, coil 24V, with transformer: 15A at 208V, 240V, 347V |  |
| KIT-ODBA-TRIAC-600 | TRIAC | Single-pole electronic relay, coil 24V, without transformer, 6A at 600V max. |  |

* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover.

1 These 2-wire relays with transformer can't supply of 3-wire low voltage thermostats.

2 "Off" position.

3 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect.

### Others

| Type | Quantity | Model et description Complementary informations | Volts | Phase | Watts | Length mm/in. | Informations Color/installation |
| --- | --- | --- | --- | --- | --- | --- | --- |

- Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Eectrician Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact in Ouellet: |  |
| Comments: |  |