Series

ODS	Ceiling Fan Heater

Features

Color	-	Standard: white, almond.

- Optional (upcharge applicable): metallic silver, bronze, metallic charcoal,

aluminum, semi-gloss black.

- Custom colors available upon request.

Finish	-	Standard: epoxy/polyester powder paint.

Voltage	-	208V, 240V, 277V, 347V, 480V, 600V, 1 or-3 phase.

Construction	-	Outlet grille made of flat ribbon wire.

-	High-limit temperature control with automatic reset.

Fan	-	Totally enclosed and lifetime-lubricated ball bearing motor.

-	Fan delay purges heater of residual heat.

Heating element	-	Three stainless steel tubular heating elements with aluminum fins.

Control	-	240/208V control circuit standard (except for 2 to 5kW at 277V have

277V control standard).

-	Built-in 240V contactor for some models (see table).

-	24V and 120V control circuit available.

-	Built-in tamperproof thermostat available.

-	24V relay (with or without transformer) available.

-	Continuous circulation controlled by a built-in switch with power-on indicator

light available (-CV).

Any remote thermostat or relay must be connected to the heater control terminal block.

Installation	-	Recommended height: between 8 ft. (2.4 m) and 12 ft. (3.6 m).

-	Recessed into insulated or T-bar ceiling (ODSR).

-	Surface mounting (ODSA and ODSB), T-BAR adaptor optional.

Note: We recommend installing this product on an outside ceiling to avoid vibrations spreading

to an adjacent room.

Warranty	-	5-year warranty against defects.

Application	-	Apartment building, commercial building, drop ceiling, stairwell, garage.

Models

| Watts | Volts (ph) | Product # | Qty | Volts (ph) | Product # | Qty | cfm | Temperature Rise |  | Motor |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | °C | °F | HP | rpm |
| ODSA Surface |  |  |  |  |  |  |  |  |  |  |  |
| 2000 | 240 (1) | ODSAU02000 |  | 240 (3) | ODSAU020301 |  | 310 | 11 | 20 | 1/50 | 1550 |
| 3000 | 240 (1) | ODSAU03000 |  | 240 (3) | ODSAU030301 |  | 310 | 17 | 30 | 1/50 | 1550 |
| 4000 | 240 (1) | ODSAU04000 |  | 240 (3) | ODSAU040301 |  | 310 | 23 | 41 | 1/50 | 1550 |
| 5000 | 240 (1) | ODSAU050001 |  | 240 (3) | ODSAU050301 |  | 310 | 28 | 51 | 1/50 | 1550 |
| 2000 | 208 (1) | ODSAU02008 |  | 208 (3) | ODSAU020381 |  | 310 | 11 | 20 | 1/50 | 1550 |
| 3000 | 208 (1) | ODSAU03008 |  | 208 (3) | ODSAU030381 |  | 310 | 17 | 30 | 1/50 | 1550 |
| 4000 | 208 (1) | ODSAU04008 |  | 208 (3) | ODSAU040381 |  | 310 | 23 | 41 | 1/50 | 1550 |
| 5000 | 208 (1) | ODSAU050081 |  | 208 (3) | ODSAU050381 |  | 310 | 28 | 51 | 1/50 | 1550 |
| 2000 | 277 (1) | ODSAU02077 |  | - | - |  | 310 | 11 | 20 | 1/50 | 1550 |
| 3000 | 277 (1) | ODSAU03077 |  | - | - |  | 310 | 17 | 30 | 1/50 | 1550 |
| 4000 | 277 (1) | ODSAU04077 |  | - | - |  | 310 | 23 | 41 | 1/50 | 1550 |
| 5000 | 277 (1) | ODSAU05077 |  | - | - |  | 310 | 28 | 51 | 1/50 | 1550 |
| 2000 | 480 (1) | ODSAU020041 |  | 480 (3) | ODSAU020341 |  | 310 | 11 | 20 | 1/50 | 1550 |
| 3000 | 480 (1) | ODSAU030041 |  | 480 (3) | ODSAU030341 |  | 310 | 17 | 30 | 1/50 | 1550 |
| 4000 | 480 (1) | ODSAU040041 |  | 480 (3) | ODSAU040341 |  | 310 | 23 | 41 | 1/50 | 1550 |
| 5000 | 480 (1) | ODSAU050041 |  | 480 (3) | ODSAU050341 |  | 310 | 28 | 51 | 1/50 | 1550 |
| ODSB Surface |  |  |  |  |  |  |  |  |  |  |  |
| 7500 | 240 (1) | ODSBU075001 |  | 240 (3) | ODSBU075301 |  | 600 | 22 | 39 | 1/33 | 1550 |
| 10000 | 240 (1) | ODSBU100001 |  | 240 (3) | ODSBU100301 |  | 600 | 29 | 53 | 1/33 | 1550 |
| 7500 | 208 (1) | ODSBU075081 |  | 208 (3) | ODSBU075381 |  | 600 | 22 | 39 | 1/33 | 1550 |
| 9900 | 208 (1) | ODSBU099081 |  | 208 (3) | ODSBU099381 |  | 600 | 29 | 53 | 1/33 | 1550 |
| 7500 | 277 (1) | ODSBU075771 |  | 347 (1) | - |  | 600 | 22 | 39 | 1/33 | 1550 |
| 10000 | 277 (1) | ODSBU100771 |  | 347 (1) | - |  | 600 | 29 | 53 | 1/33 | 1550 |
| 7500 | 480 (1) | ODSBU075041 |  | 480 (3) | ODSBU075341 |  | 600 | 22 | 39 | 1/33 | 1550 |
| 10000 | 480 (1) | ODSBU100041 |  | 480 (3) | ODSBU100341 |  | 600 | 29 | 53 | 1/33 | 1550 |
| ODSR Recessed |  |  |  |  |  |  |  |  |  |  |  |
| 2000 | 240 (1) | ODSRU02000 |  | 240 (3) | ODSRU020301 |  | 310 | 11 | 20 | 1/50 | 1550 |
| 3000 | 240 (1) | ODSRU03000 |  | 240 (3) | ODSRU030301 |  | 310 | 17 | 39 | 1/50 | 1550 |
| 4000 | 240 (1) | ODSRU04000 |  | 240 (3) | ODSRU040301 |  | 310 | 23 | 41 | 1/50 | 1550 |
| 5000 | 240 (1) | ODSRU050001 |  | 240 (3) | ODSRU050301 |  | 310 | 28 | 51 | 1/50 | 1550 |
| 2000 | 208 (1) | ODSRU02008 |  | 208 (3) | ODSRU020381 |  | 310 | 11 | 20 | 1/50 | 1550 |
| 3000 | 208 (1) | ODSRU03008 |  | 208 (3) | ODSRU030381 |  | 310 | 17 | 30 | 1/50 | 1550 |
| 4000 | 208 (1) | ODSRU04008 |  | 208 (3) | ODSRU040381 |  | 310 | 23 | 41 | 1/50 | 1550 |
| 5000 | 208 (1) | ODSRU050081 |  | 208 (3) | ODSRU050381 |  | 310 | 28 | 51 | 1/50 | 1550 |
| 2000 | 277 (1) | ODSRU02077 |  | - | - |  | 310 | 11 | 20 | 1/50 | 1550 |
| 3000 | 277 (1) | ODSRU03077 |  | - | - |  | 310 | 17 | 30 | 1/50 | 1550 |
| 4000 | 277 (1) | ODSRU04077 |  | - | - |  | 310 | 23 | 41 | 1/50 | 1550 |
| 5000 | 277 (1) | ODSRU05077 |  | - | - |  | 310 | 28 | 51 | 1/50 | 1550 |
| 2000 | 480 (1) | ODSRU020041 |  | 480 (3) | ODSRU020341 |  | 310 | 11 | 20 | 1/50 | 1550 |
| 3000 | 480 (1) | ODSRU030041 |  | 480 (3) | ODSRU030341 |  | 310 | 17 | 30 | 1/50 | 1550 |
| 4000 | 480 (1) | ODSRU040041 |  | 480 (3) | ODSRU040341 |  | 310 | 23 | 41 | 1/50 | 1550 |
| 5000 | 480 (1) | ODSRU050041 |  | 480 (3) | ODSRU050341 |  | 310 | 28 | 51 | 1/50 | 1550 |

### Options

| Product # Kit | Product # Factory installed* | Description | Qty |
| --- | --- | --- | --- |
| - | 120 | 120V control circuit |  |
| - | CV | Summer fan switch and pilot light |  |
| KIT-ODS-DIS202 | DIS202 | Disconnect switch, double-pole, 20A at 277V and less |  |
| KIT-ODS-DIS402 | DIS402 | Disconnect switch, triple-pole, 40A at 600V max. |  |
| - | DIS802 | Disconnect switch, triple-pole, 80A at 600V |  |
| KIT-ODS-R | R | 24V control relay, without transformer |  |
| - | RCV24 | Summer fan relay 24V, remote control and pilot light (switch not included) |  |
| - | RCV240 | Summer fan relay 240V, remote control and pilot light (switch not included) |  |
| - | RT | 24V control relay, with transformer |  |
| KIT-ODS-T-AV | TAV | Thermostat tamperproof |  |
| KIT-ODSA-T-BAR | - | Adaptor for T-bar ceiling, ODSA only |  |
| KIT-ODSB-T-BAR | - | Adaptor for T-bar ceiling, ODSB only |  |

* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover.

1 Built-in 240V contactor.

2 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect.

### Others

| Type | Quantity | Model et description Complementary informations | Volts | Phase | Watts | Length mm/in. | Informations Color/installation |
| --- | --- | --- | --- | --- | --- | --- | --- |

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Eectrician Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact in Ouellet: |  |
| Comments: |  |