- Series

OHV	Commercial Unit Heater

- Features

Color	-	Standard: almond.

Finish	-	Standard: epoxy/polyester powder paint.

Voltage	-	208V, 240V, 277V, 347V, 480V, 600V, 1 or 3-phase.

Construction	-	Draw-through design for more evenly heated air.

-	Specially designed outlet diffuser provides maximum

air velocity.

-	Individually adjustable louvers to direct discharge air flow.

-	High-limit temperature control with automatic reset.

-	18 and 20 gauge steel.

Fan	-	Motor - totally enclosed - thermally protected.

-	Motor mounted in ambient air stream,

shielded from heating elements.

-	Fan delay purges heater of residual heat for longer life.

Heating element	-	Stainless steel sheath with aluminum fins.

-	Draw-through design permits greater heat transfer.

Control	-	All models have factory installed contactor.

-	240/208V control circuit standard on all models (with transformer if needed).

-	Full line of unit mounted control accessories available

(factory or field installed).

Installation	-	Minimum mounting height of 8 ft. (2.4 m.)

-	Horizontal or vertical discharge air flow.

-	Includes wall and ceiling mounting brackets

(for horizontal discharge air flow).

- For vertical air ﬂow 4 welded nuts (for threaded rod 3/8 in. X 16 UNC)

provided in heater back.

-	Large and easily accessible control compartment.

Note: We recommend installing this product on an outside ceiling or wall to avoid vibrations spreading

to an adjacent room.

Warranty	-	5-year warranty against defects.

Application 	-	Factory, warehouse, garage, store, shipping room.

- Models

| Product # | Qty | Volts (ph) | kW | BTU/hr | cfm | Temperature Rise |  | Motor |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | °C | °F | HP | rpm |
| OHV02008AM |  | 208 (1/31) | 2.0 | 6824 | 310 | 11 | 20 | 1/50 | 1490 |
| OHV02038AM |  | 208 (3) | 2.0 | 6824 | 310 | 11 | 20 | 1/50 | 1490 |
| OHV03008AM |  | 208 (1/31) | 3.0 | 10236 | 310 | 17 | 31 | 1/50 | 1490 |
| OHV03038AM |  | 208 (3) | 3.0 | 10236 | 310 | 17 | 31 | 1/50 | 1490 |
| OHV05008AM |  | 208 (1/31) | 5.0 | 17060 | 310 | 28 | 50 | 1/50 | 1490 |
| OHV05038AM |  | 208 (3) | 5.0 | 17060 | 310 | 28 | 50 | 1/50 | 1490 |
| OHV07508AM |  | 208 (1/31) | 7.5 | 25590 | 600 | 22 | 40 | 1/33 | 1490 |
| OHV07538AM |  | 208 (3) | 7.5 | 25590 | 600 | 22 | 40 | 1/33 | 1490 |
| OHV10008AM |  | 208 (1/31) | 10.0 | 34120 | 600 | 29 | 52 | 1/33 | 1490 |
| OHV10038AM |  | 208 (3) | 10.0 | 34120 | 600 | 29 | 52 | 1/33 | 1490 |
| OHV15038AM |  | 208 (3) | 15.0 | 51180 | 915 | 29 | 52 | 1/8 | 1490 |
| OHV20038AM |  | 208 (3) | 20.0 | 68240 | 1250 | 28 | 50 | 1/8 | 1490 |
| OHV02000AM |  | 240/208 (1/31) | 2.0/1.5 | 6824/5118 | 310 | 11 | 20 | 1/50 | 1550 |
| OHV03000AM |  | 240/208 (1/31) | 3.0/2.3 | 10236/7848 | 310 | 17 | 31 | 1/50 | 1550 |
| OHV05000AM |  | 240/208 (1/31) | 5.0/3.75 | 17060/12966 | 310 | 28 | 50 | 1/50 | 1550 |
| OHV07500AM |  | 240/208 (1/31) | 7.5/5.6 | 25590/19200 | 625 | 21 | 38 | 1/33 | 1550 |
| OHV10000AM |  | 240/208 (1/31) | 10.0/7.5 | 34120/25590 | 625 | 28 | 50 | 1/33 | 1550 |
| OHV15030AM |  | 240/208 (3) | 15.0/11.3 | 51180/38387 | 950 | 28 | 50 | 1/8 | 1550 |
| OHV20030AM |  | 240/208 (3) | 20.0/15.0 | 68240/51180 | 1300 | 27 | 49 | 1/8 | 1550 |
| OHV02007AM |  | 347 (1) | 2.0 | 6824 | 310 | 11 | 20 | 1/50 | 1550 |
| OHV03007AM |  | 347 (1) | 3.0 | 10236 | 310 | 17 | 31 | 1/50 | 1550 |
| OHV05007AM |  | 347 (1) | 5.0 | 17060 | 310 | 28 | 50 | 1/50 | 1550 |
| OHV07507AM |  | 347 (1) | 7.5 | 25590 | 625 | 21 | 38 | 1/33 | 1550 |
| OHV10007AM |  | 347 (1) | 10.0 | 34120 | 625 | 28 | 50 | 1/33 | 1550 |
| OHV02006AM |  | 600 (1) | 2.0 | 6824 | 310 | 11 | 20 | 1/50 | 1550 |
| OHV02036AM |  | 600 (3) | 2.0 | 6824 | 310 | 11 | 20 | 1/50 | 1550 |
| OHV03006AM |  | 600 (1) | 3.0 | 10236 | 310 | 17 | 31 | 1/50 | 1550 |
| OHV03036AM |  | 600 (3) | 3.0 | 10236 | 310 | 17 | 31 | 1/50 | 1550 |
| OHV05006AM |  | 600 (1) | 5.0 | 17060 | 310 | 28 | 50 | 1/50 | 1550 |
| OHV05036AM |  | 600 (3) | 5.0 | 17060 | 310 | 28 | 50 | 1/50 | 1550 |
| OHV07536AM |  | 600 (3) | 7.5 | 25590 | 625 | 21 | 38 | 1/33 | 1550 |
| OHV10036AM |  | 600 (3) | 10.0 | 34120 | 625 | 28 | 50 | 1/33 | 1550 |
| OHV15036AM |  | 600 (3) | 15.0 | 51180 | 950 | 28 | 50 | 1/8 | 1550 |
| OHV20036AM |  | 600 (3) | 20.0 | 68240 | 1300 | 27 | 49 | 1/8 | 1550 |

1 Models with the indication "1/3" can be field converted from 1 to 3-phase.

Standard color is almond.

277V and 480V available upon request.

- Options

| Product # Kit | Product # Factory installed* | Description | Qty |
| --- | --- | --- | --- |
| - | 120 | 120V control circuit |  |
| - | 24 | 24V control circuit |  |
| - | 3P | Triple-pole contactor |  |
| KIT-OHV-D41 | D41 | Disconnect switch, triple-pole, 40A |  |
| KIT-OHV-D81 | D81 | Disconnect switch, triple-pole, 80A |  |
| KIT-OHV-F1 | F1 | Continuous fan switch, for 2 to 5kW units |  |
| KIT-OHV-F2 | F2 | Continuous fan switch with 24V relay, for units with 24V control circuit |  |
| KIT-OHV-F3 | F3 | Continuous fan switch, for less than 480V units (7.5 to 20kW) |  |
| KIT-OHV-F4 | F4 | Continuous fan switch, for 480V units and over (7.5 to 20kW) |  |
| KIT-OHV-FR | FR | Unit mounted fan relay for remote fan control of heaters with 24V control circuit (remote fan switch not included) |  |
| - | FUS | Branch circuit fusing |  |
| - | HL | Hi/Lo switch (15 to 20kW) |  |
| KIT-OHV-R | R | 24V relay, without transformer |  |
| KIT-OHV-RT | RT | 24V relay, with transformer |  |
| KIT-OHV-T2S | T2S | 2-stage thermostat (15 to 20kW) |  |
| KIT-OHV-T5 | T5 | Single-stage thermostat, for 10kW units and less |  |
| KIT-OHV-T6 | T6 | Single-stage thermostat, for units over 10kW |  |

* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover.

1 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect.

- Others

| Type | Quantity | Model and description Complementary information | Volts | Phase | Watts | Length mm/in. | Information Color/installation |
| --- | --- | --- | --- | --- | --- | --- | --- |

- Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrician Contractor: |  |
| Distributor: |  |
| Date : |  |
| Contact in Ouellet: |  |
| Comments: |  |