- Series

OHV	Commercial Unit Heater

- Features

Color	-	Standard: almond.

Finish	-	Standard: epoxy/polyester powder paint.

Voltage	-	208V, 240V, 277V, 347V, 480V, 600V, 1 or 3-phase.

Construction	-	Draw-through design for more evenly heated air.

-	Specially designed outlet diffuser provides maximum

air velocity.

-	Individually adjustable louvers to direct discharge air flow.

-	High-limit temperature control with automatic reset.

-	18 and 20 gauge steel.

Fan	-	Motor - totally enclosed - thermally protected.

-	Motor mounted in ambient air stream,

shielded from heating elements.

-	Fan delay purges heater of residual heat for longer life.

Heating element	-	Stainless steel sheath with aluminum fins.

- Draw-through design permits greater heat transfer.

Control	-	All models have factory installed contactor.

- 24V control circuit standard on all models (except 2, 3 & 5kW, 208/240V heaters).

- 2, 3 & 5kW, 208/240V heaters have 208/240V control (24V control available).

- Full line of unit mounted control accessories available (factory or field installed).

Installation	-	Minimum mounting height of 6 ft. (1.8 m.)

- Horizontal or vertical discharge air flow.

- Includes wall and ceiling mounting brackets (for horizontal discharge air flow).

- For vertical air flow 4 welded nuts (for threaded rod 3/8 in. X 16 UNC)

provided in heater back.

- Large and easily accessible control compartment.

Note: We recommend installing this product on an outside ceiling or wall to avoid vibrations spreading to an adjacent room.

Warranty	-	5-year warranty against defects.

Application 	-	Factory, warehouse, garage, store, shipping room.

- Models

| Product # | Qty | Volts (ph) | kW | Control Voltage | BTU/hr | cfm | Temperature Rise |  | Motor |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | °C | °F | HP | rpm |
| OHVU02008AM |  | 208 (1/31) | 2.0 | 240/208 | 6824 | 310 | 11 | 20 | 1/50 | 1490 |
| OHVU03008AM |  | 208 (1/31) | 3.0 | 240/208 | 10236 | 310 | 17 | 31 | 1/50 | 1490 |
| OHVU05008AM |  | 208 (1/31) | 5.0 | 240/208 | 17060 | 310 | 28 | 51 | 1/50 | 1490 |
| OHVU07508AM-24 |  | 208 (1/31) | 7.5 | 24 | 25590 | 600 | 22 | 40 | 1/33 | 1490 |
| OHVU09908AM-24 |  | 208 (1/31) | 9.9 | 24 | 33780 | 600 | 29 | 52 | 1/33 | 1490 |
| OHVU15038AM-24 |  | 208 (3) | 15 | 24 | 51180 | 915 | 29 | 52 | 1/8 | 1490 |
| OHVU02000AM |  | 240/208 (1/31) | 2.0/1.5 | 240/208 | 6824/5118 | 310 | 11 | 20 | 1/50 | 1550 |
| OHVU03000AM |  | 240/208 (1/31) | 3.0/2.3 | 240/208 | 10236/7848 | 310 | 17 | 31 | 1/50 | 1550 |
| OHVU05000AM |  | 240/208 (1/31) | 5.0/3.75 | 240/208 | 17060/12966 | 310 | 28 | 51 | 1/50 | 1550 |
| OHVU07500AM-24 |  | 240/208 (1/31) | 7.5/5.6 | 24 | 25590/19200 | 625 | 21 | 38 | 1/33 | 1550 |
| OHVU10000AM-24 |  | 240/208 (1/31) | 10.0/7.5 | 24 | 34120/25590 | 625 | 28 | 51 | 1/33 | 1550 |
| OHVU15030AM-24 |  | 240/208 (3) | 15.0/11.3 | 24 | 51180/38387 | 950 | 28 | 50 | 1/8 | 1550 |
| OHVU19830AM-24 |  | 240/208 (3) | 19.8/14.9 | 24 | 67560/50840 | 1300 | 27 | 49 | 1/8 | 1550 |
| OHVU02077AM-24 |  | 277 (1) | 2.0 | 24 | 6824 | 310 | 11 | 20 | 1/50 | 1550 |
| OHVU03077AM-24 |  | 277 (1) | 3.0 | 24 | 10236 | 310 | 17 | 31 | 1/50 | 1550 |
| OHVU05077AM-24 |  | 277 (1) | 5.0 | 24 | 17060 | 310 | 28 | 51 | 1/50 | 1550 |
| OHVU07577AM-24 |  | 277 (1) | 7.5 | 24 | 25590 | 625 | 21 | 38 | 1/33 | 1550 |
| OHVU10077AM-24 |  | 277 (1) | 10.0 | 24 | 34120 | 625 | 28 | 51 | 1/33 | 1550 |
| OHVU02034AM-242 |  | 480 (3) | 2.0 | 24 | 6824 | 310 | 11 | 20 | 1/50 | 1550 |
| OHVU03034AM-242 |  | 480 (3) | 3.0 | 24 | 10236 | 310 | 17 | 31 | 1/50 | 1550 |
| OHVU05034AM-242 |  | 480 (3) | 5.0 | 24 | 17060 | 310 | 28 | 51 | 1/50 | 1550 |
| OHVU07534AM-242 |  | 480 (3) | 7.5 | 24 | 25590 | 625 | 21 | 38 | 1/33 | 1550 |
| OHVU10034AM-24 |  | 480 (3) | 10.0 | 24 | 34120 | 625 | 28 | 51 | 1/33 | 1550 |
| OHVU15034AM-24 |  | 480 (3) | 15.0 | 24 | 51180 | 950 | 28 | 50 | 1/8 | 1550 |
| OHVU20034AM-24 |  | 480 (3) | 20.0 | 24 | 68240 | 1300 | 27 | 49 | 1/8 | 1550 |

1 Models with the indication "1/3" can be field converted from 1 to 3-phase.

2 480V, 1-phase available upon request.

Remember to change the 3 for 0 when ordering. E.g.: OHVU05034AM-24 becomes OHVU05004AM-24.

600V available upon request.

Mounting hardware included.

Standard color is almond.

- Options

| Product # Kit | Product # Factory installed* | Description | Qty |
| --- | --- | --- | --- |
| - | 120 | 120V control circuit |  |
| - | 24 | 24V control circuit |  |
| - | 3P | Triple-pole contactor |  |
| KIT-OHV-D41 | D41 | Disconnect switch, triple-pole, 40A |  |
| KIT-OHV-D81 | D81 | Disconnect switch, triple-pole, 80A |  |
| KIT-OHV-F1 | F1 | Continuous fan switch, for 2 to 5kW units |  |
| KIT-OHV-F2 | F2 | Continuous fan switch with 24V relay, for units with 24V control circuit |  |
| KIT-OHV-F3 | F3 | Continuous fan switch, for less than 480V units (7.5 to 20kW) |  |
| KIT-OHV-F4 | F4 | Continuous fan switch, for 480V units and over (7.5 to 20kW) |  |
| KIT-OHV-FR | FR | Unit mounted fan relay for remote fan control of heaters with 24V control circuit (remote fan switch not included) |  |
| - | FUS | Branch circuit fusing |  |
| - | HL | Hi/Lo switch (15 to 20kW) |  |
| KIT-OHV-R | R | 24V relay, without transformer |  |
| KIT-OHV-RT | RT | 24V relay, with transformer |  |
| KIT-OHV-T2S | T2S | 2-stage thermostat (15 to 20kW) |  |
| KIT-OHV-T5 | T5 | Single-stage thermostat, for 10kW units and less |  |
| KIT-OHV-T6 | T6 | Single-stage thermostat, for units over 10kW |  |

* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover.

1 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect.

- Others

| Type | Quantity | Model and description Complementary information | Volts | Phase | Watts | Length mm/in. | Information Color/installation |
| --- | --- | --- | --- | --- | --- | --- | --- |

- Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrician Contractor: |  |
| Distributor: |  |
| Date : |  |
| Contact in Ouellet: |  |
| Comments: |  |