Series

OPH	Plenum Rated Unit Heater

Features

Color	-	Standard: aluminum.

Finish	-	Standard: epoxy/polyester powder paint.

Voltage	-	208V, 240V, 277V, 347V, 480V, 600V, 1 or 3-phase.

Construction	-	18 and 20-gauge steel.

-	Adjustable louver for air flow direction available.

-  Automatic reset and manual reset high-limit temperature control.

-  One contactor per high-limit temperature control, on independent circuit.

Fan	-	Direct drive, selectable speed squirrel-cage fan.

- Fan delay.

Motor	-	Totally enclosed standard factory-lubricated motor.

- Thermally protected motor mounted in cold compartment.

- Constant torque motor (ECM), 1/3 HP max., 1050 rpm max., available.

Heating element	-	Three tubular heating elements with ﬁns (for 3.1kW-5kW-7.5kW models).

-  Six tubular heating elements with fins (for 10kW-12kW-15kW models).

Control	-	Factory-installed contactor and 240/208V control circuit standard.*

-  Factory-installed disconnect switch.

-	24V control circuit, with transformer available.*

-	120V control circuit with transformer available.*

- 	Built-in thermostat available.

-  Optional 2-stage thermostat (for 10kW-12kW-15kW models).

Ouellet highly recommends to use a wall thermostat for greater comfort.

Any remote thermostat or relay must be connected to the heater control terminal block.
*Two stage heat with 2-stage thermostat available for 10kW to 15kW models.

Installation	-		Horizontal mounting with free air discharge or ducted installation.

-	Vertical mounting in the upwards air flow position with ducted installation only
(3.1kW and 5kW models only).

-	27 °C (80 °F) maximum operating ambient temperature.

-	Zero clearance approved when installed in concealed space.

Warranty	-  3-year warranty against defects.

Application 	-	This heater is designed to be used in the space between a structural ceiling

and a suspended ceiling, plenum space or plenum.

- Crawl space, commercial vestibule, office, commercial building, warehouse, stairwell,

underground parking.

Models

| Product # | Qty | Volts | Phase | kW (BTU/hr) | cfm min.¹ |  | Temperature Rise² |  | Motor |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Low Speed | High Speed | oC | oF | HP | rpm |
| OPH03108AL-DIS40 |  | 208 | 1 | 3.1 (10578) | 430 | 460 | 12 | 22 | 1/3 | 1075 |
| OPH03138AL-DIS40 |  | 208 | 3 | 3.1 (10578) | 430 | 460 | 12 | 22 | 1/3 | 1075 |
| OPH03100AL-DIS40 |  | 240 | 1 | 3.1 (10578) | 430 | 460 | 12 | 22 | 1/3 | 1075 |
| OPH03130AL-DIS40 |  | 240 | 3 | 3.1 (10578) | 430 | 460 | 12 | 22 | 1/3 | 1075 |
| OPH03177AL-DIS40 |  | 277 | 1 | 3.1 (10578) | 430 | 460 | 12 | 22 | 1/3 | 1075 |
| OPH03107AL-DIS40 |  | 347 | 1 | 3.1 (10578) | 430 | 460 | 12 | 22 | 1/3 | 1075 |
| OPH03104AL-DIS40 |  | 480 | 1 | 3.1 (10578) | 430 | 460 | 12 | 22 | 1/3 | 1075 |
| OPH03134AL-DIS40 |  | 480 | 3 | 3.1 (10578) | 430 | 460 | 12 | 22 | 1/3 | 1075 |
| OPH03106AL-DIS40 |  | 600 | 1 | 3.1 (10578) | 430 | 460 | 12 | 22 | 1/3 | 1075 |
| OPH03136AL-DIS40 |  | 600 | 3 | 3.1 (10578) | 430 | 460 | 12 | 22 | 1/3 | 1075 |
| OPH05008AL-DIS40 |  | 208 | 1 | 5 (17060) | 430 | 460 | 21 | 37 | 1/3 | 1075 |
| OPH05038AL-DIS40 |  | 208 | 3 | 5 (17060) | 430 | 460 | 21 | 37 | 1/3 | 1075 |
| OPH05000AL-DIS40 |  | 240 | 1 | 5 (17060) | 430 | 460 | 21 | 37 | 1/3 | 1075 |
| OPH05030AL-DIS40 |  | 240 | 3 | 5 (17060) | 430 | 460 | 21 | 37 | 1/3 | 1075 |
| OPH05077AL-DIS40 |  | 277 | 1 | 5 (17060) | 430 | 460 | 21 | 37 | 1/3 | 1075 |
| OPH05007AL-DIS40 |  | 347 | 1 | 5 (17060) | 430 | 460 | 21 | 37 | 1/3 | 1075 |
| OPH05004AL-DIS40 |  | 480 | 1 | 5 (17060) | 430 | 460 | 21 | 37 | 1/3 | 1075 |
| OPH05034AL-DIS40 |  | 480 | 3 | 5 (17060) | 430 | 460 | 21 | 37 | 1/3 | 1075 |
| OPH05006AL-DIS40 |  | 600 | 1 | 5 (17060) | 430 | 460 | 21 | 37 | 1/3 | 1075 |
| OPH05036AL-DIS40 |  | 600 | 3 | 5 (17060) | 430 | 460 | 21 | 37 | 1/3 | 1075 |
| OPH07508AL-DIS80 |  | 208 | 1 | 7.5 (25591) | 1100 | 1200 | 14 | 25 | 1/3 | 1075 |
| OPH07538AL-DIS40 |  | 208 | 3 | 7.5 (25591) | 1100 | 1200 | 14 | 25 | 1/3 | 1075 |
| OPH07500AL-DIS40 |  | 240 | 1 | 7.5 (25591) | 1100 | 1200 | 14 | 25 | 1/3 | 1075 |
| OPH07530AL-DIS40 |  | 240 | 3 | 7.5 (25591) | 1100 | 1200 | 14 | 25 | 1/3 | 1075 |
| OPH07577AL-DIS40 |  | 277 | 1 | 7.5 (25591) | 1100 | 1200 | 14 | 25 | 1/3 | 1075 |
| OPH07507AL-DIS40 |  | 347 | 1 | 7.5 (25591) | 1100 | 1200 | 14 | 25 | 1/3 | 1075 |
| OPH07504AL-DIS40 |  | 480 | 1 | 7.5 (25591) | 1100 | 1200 | 14 | 25 | 1/3 | 1075 |
| OPH07534AL-DIS40 |  | 480 | 3 | 7.5 (25591) | 1100 | 1200 | 14 | 25 | 1/3 | 1075 |
| OPH07506AL-DIS40 |  | 600 | 1 | 7.5 (25591) | 1100 | 1200 | 14 | 25 | 1/3 | 1075 |
| OPH07536AL-DIS40 |  | 600 | 3 | 7.5 (25591) | 1100 | 1200 | 14 | 25 | 1/3 | 1075 |
| OPH10038AL-DIS40 |  | 208 | 3 | 10 (34121) | 1100 | 1200 | 18 | 32 | 1/3 | 1075 |
| OPH10000AL-DIS80 |  | 240 | 1 | 10 (34121) | 1100 | 1200 | 18 | 32 | 1/3 | 1075 |
| OPH10030AL-DIS40 |  | 240 | 3 | 10 (34121) | 1100 | 1200 | 18 | 32 | 1/3 | 1075 |
| OPH10077AL-DIS80 |  | 277 | 1 | 10 (34121) | 1100 | 1200 | 18 | 32 | 1/3 | 1075 |
| OPH10007AL-DIS40 |  | 347 | 1 | 10 (34121) | 1100 | 1200 | 18 | 32 | 1/3 | 1075 |
| OPH10004AL-DIS40 |  | 480 | 1 | 10 (34121) | 1100 | 1200 | 18 | 32 | 1/3 | 1075 |
| OPH10034AL-DIS40 |  | 480 | 3 | 10 (34121) | 1100 | 1200 | 18 | 32 | 1/3 | 1075 |
| OPH10006AL-DIS40 |  | 600 | 1 | 10 (34121) | 1100 | 1200 | 18 | 32 | 1/3 | 1075 |
| OPH10036AL-DIS40 |  | 600 | 3 | 10 (34121) | 1100 | 1200 | 18 | 32 | 1/3 | 1075 |
| OPH12038AL-DIS80 |  | 208 | 3 | 12 (40945) | 1100 | 1200 | 22 | 40 | 1/3 | 1075 |
| OPH12030AL-DIS40 |  | 240 | 3 | 12 (40945) | 1100 | 1200 | 22 | 40 | 1/3 | 1075 |
| OPH12007AL-DIS80 |  | 347 | 1 | 12 (40945) | 1100 | 1200 | 22 | 40 | 1/3 | 1075 |
| OPH12004AL-DIS40 |  | 480 | 1 | 12 (40945) | 1100 | 1200 | 22 | 40 | 1/3 | 1075 |
| OPH12034AL-DIS40 |  | 480 | 3 | 12 (40945) | 1100 | 1200 | 22 | 40 | 1/3 | 1075 |
| OPH12006AL-DIS40 |  | 600 | 1 | 12 (40945) | 1100 | 1200 | 22 | 40 | 1/3 | 1075 |
| OPH12036AL-DIS40 |  | 600 | 3 | 12 (40945) | 1100 | 1200 | 22 | 40 | 1/3 | 1075 |
| OPH15038AL-DIS80 |  | 208 | 3 | 15 (51182) | 1100 | 1200 | 27 | 49 | 1/3 | 1075 |
| OPH15030AL-DIS80 |  | 240 | 3 | 15 (51182) | 1100 | 1200 | 27 | 49 | 1/3 | 1075 |
| OPH15004AL-DIS40 |  | 480 | 1 | 15 (51182) | 1100 | 1200 | 27 | 49 | 1/3 | 1075 |
| OPH15034AL-DIS40 |  | 480 | 3 | 15 (51182) | 1100 | 1200 | 27 | 49 | 1/3 | 1075 |
| OPH15006AL-DIS40 |  | 600 | 1 | 15 (51182) | 1100 | 1200 | 27 | 49 | 1/3 | 1075 |
| OPH15036AL-DIS40 |  | 600 | 3 | 15 (51182) | 1100 | 1200 | 27 | 49 | 1/3 | 1075 |

¹ Tested at 0.2’’ water column (static pressure).

2 Tested at low speed.

Standard color is aluminum.

Options

| Product # Kit | Product # Factory installed* | Description | Qty |
| --- | --- | --- | --- |
| - | 24 | 24V control circuit |  |
| - | 1201 | 120V control circuit |  |
| - | OL | Power indicator light |  |
| - | ECM² | Constant torque motor (ECM), 1/3 HP max., 1050 rpm max. |  |
| KIT-OPH-3-5KW-FI | FI | Pleated air filter for 3-5kW models |  |
| KIT-OPH-3-5KW-FIW | FIW | Washable air filter for 3-5kW models |  |
| KIT-OPH-3-5KW-LR | LR | Louver kit for 3-5kW models |  |
| KIT-OPH-3-5KW-T | T | Built-in thermostat for 3-5kW models |  |
| KIT-OPH-7-15KW-FI | FI | Pleated air filter for 7-15kW models |  |
| KIT-OPH-7-15KW-FIW | FIW | Washable air filter for 7-15kW models |  |
| KIT-OPH-7-15KW-LR | LR | Louver kit for 7-15kW models |  |
| KIT-OPH-7-15KW-T | T | Built-in thermostat for 7-15kW models |  |
| KIT-OPH-T2S | T2S | Built-in 2-stage thermostat for 10-15kW models only |  |

1 With basic control or with the option «-120», the fan will work at low speed only.

2 Built-in transformer and contactor for 24V are required, add « -24 » to the product number.

* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover.

### Others

| Type | Quantity | Model et description Complementary informations | Volts | Phase | Watts | Length mm/in. | Informations Color/installation |
| --- | --- | --- | --- | --- | --- | --- | --- |

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrician Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact in Ouellet: |  |
| Comments: |  |