- Series

ORA-C	C Range Commercial Air Curtain

- Features

Model	-	Electric heat.

-	No heat.

Color	-	Standard: white.

- Custom colors available upon request (RAL Chart).

Voltage	-	208V, 240/208V, 480V, 600V, 60 Hz.

Construction	-	Steel casing with resistant plastic end caps.

-	Quick access to the internal components thanks to the front panel which facilitate maintenance and connection.

-	High-limit temperature control with automatic reset.

Fan	-	Tangential fans.

Heating element	-	Element provides instant heat (electric model).

Control	-	Ecopower control included (20 ft. (6 m) RJ9 control included).

- Door switch included.

- Compatible with a Building Management System (Bacnet MS/TP, Modbus RTU or dry contact).

- Personalize programing of the air curtain.

Installation	- 	Minimum height installation: 6 ft. (1.8 m).

-	Maximum height installation:

- Surface-mounted: 9.84 ft. (3 m) above the floor.

- Recessed: 9 ft. (2.75 m) above the floor.

-	Surface-mounted: brackets included.

-	Ceiling hanging: fixings are included for 1/4 in. x 20 UNC threaded rods (rods not supplied).

-	Recessed: hinged core grilles included for easy installation and maintenance.

-	Joining kit, available in option, for connecting multiple surface mounted units.

Warranty	-	2-year warranty against defects.

Application	-	Vestibule, commercial building, entrance way, service door, hospital.

- IMPORTANT: 600V and 480V models need 2 power sources (E.g.: 600V+208V or 230V) or an external transformer (E.g.: 600V/240V).
The VA requirement varies between models: C1000 = 200VA, C1500 and C2000 = 350VA.

- Models

| Product # | Qty | Volts (ph) |  |  | kW Lo/Hi | Amp. |  | cfm |  | Max velocity (ft./min) | dBA at 3 m | Effective width of air stream |  | Weight |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  | in. | mm | lb | kg |
| Surface-mounted |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Electric heat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C1000ESEC600V |  | 600 (3) + 208 or 2402 |  | 4.5/9 |  | 9.3+0.5 | 740 |  | 1770 |  | 55.0 | 36 | 933 | 35 | 16 |
| C1500ESEC600V |  | 600 (3) + 208 or 2402 |  | 6/12 |  | 12.8+0.7 | 1060 |  | 1770 |  | 55.0 | 56 | 1430 | 51 | 23 |
| C2000ESEC600V |  | 600 (3) + 208 or 2402 |  | 9/18 |  | 18.6+1.0 | 1470 |  | 1770 |  | 56.0 | 78 | 1996 | 73 | 33 |
| C1000ESEC480V |  | 480 (3) + 208 or 2402 |  | 4.5/9 |  | 10.9+0.5 | 740 |  | 1770 |  | 55.0 | 36 | 933 | 35 | 16 |
| C1500ESEC480V |  | 480 (3) + 208 or 2402 |  | 6/12 |  | 14.5+0.7 | 1060 |  | 1770 |  | 55.0 | 56 | 1430 | 51 | 23 |
| C2000ESEC480V |  | 480 (3) + 208 or 2402 |  | 9/18 |  | 21.7+1.0 | 1470 |  | 1770 |  | 56.0 | 78 | 1996 | 73 | 33 |
| C1000ESEC208V |  | 208 (3)3 |  | 4.32/8.64 |  | 24.5 | 740 |  | 1770 |  | 55.0 | 36 | 933 | 35 | 16 |
| C1500ESEC208V |  | 208 (3)3 |  | 5.77/11.53 |  | 32.7 | 1060 |  | 1770 |  | 55.0 | 56 | 1430 | 51 | 23 |
| C2000ESEC208V |  | 208 (3)3 |  | 8.64/17.28 |  | 49.0 | 1470 |  | 1770 |  | 56.0 | 78 | 1996 | 73 | 33 |
| No heat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C1000ASEC208-230V |  | 208/240 (1)3 | - |  |  | 0.5 |  | 740 |  | 1770 | 55.0 | 36 | 933 | 33 | 15 |
| C1500ASEC208-230V |  | 208/240 (1)3 | - |  |  | 0.7 |  | 1060 |  | 1770 | 55.0 | 56 | 1430 | 46 | 21 |
| C2000ASEC208-230V |  | 208/240 (1)3 | - |  |  | 1 |  | 1470 |  | 1770 | 56.0 | 78 | 1996 | 68 | 31 |
| Recessed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Electric heat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C1000EREC600V |  | 600 (3) + 208 or 2402 | 4.5/9 |  |  | 9.3+0.5 |  | 740 |  | 1770 | 55.0 | 45 | 1145 | 44 | 20 |
| C1500EREC600V |  | 600 (3) + 208 or 2402 | 6/12 |  |  | 12.8+0.7 |  | 1060 |  | 1770 | 55.0 | 60 | 1545 | 60 | 27 |
| C2000EREC600V |  | 600 (3) + 208 or 2402 | 9/18 |  |  | 18.6+1.0 |  | 1470 |  | 1770 | 56.0 | 80 | 2055 | 82 | 37 |
| C1000EREC480V |  | 480 (3) + 208 or 2402 | 4.5/9 |  |  | 10.9+0.5 |  | 740 |  | 1770 | 55.0 | 45 | 1145 | 44 | 20 |
| C1500EREC480V |  | 480 (3) + 208 or 2402 | 6/12 |  |  | 14.5+0.7 |  | 1060 |  | 1770 | 55.0 | 60 | 1545 | 51 | 23 |
| C2000EREC480V |  | 480 (3) + 208 or 2402 | 9/18 |  |  | 21.7+1.0 |  | 1470 |  | 1770 | 56.0 | 80 | 2055 | 73 | 33 |
| C1000EREC208V |  | 208 (3)3 | 4.32/8.64 |  |  | 24.5 |  | 740 |  | 1770 | 55.0 | 45 | 1145 | 44 | 20 |
| C1500EREC208V |  | 208 (3)3 | 5.77/11.53 |  |  | 32.7 |  | 1060 |  | 1770 | 55.0 | 60 | 1545 | 60 | 27 |
| C2000EREC208V |  | 208 (3) 3 | 8.64/17.28 |  |  | 49.0 |  | 1470 |  | 1770 | 56.0 | 80 | 2055 | 82 | 37 |
| No heat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C1000AREC208V |  | 208/240 (1)3 | - |  |  | 0.5 |  | 740 |  | 1770 | 55.0 | 45 | 1145 | 42 | 19 |
| C1500AREC208V |  | 208/240 (1)3 | - |  |  | 0.7 |  | 1060 |  | 1770 | 55.0 | 60 | 1545 | 55 | 25 |
| C2000AREC208V |  | 208/240 (1)3 | - |  |  | 1 |  | 1470 |  | 1770 | 56.0 | 80 | 2055 | 77 | 35 |

1 To order any custom colors from the R.A.L. chart, add “-SP” at the end of the Product # and specify RAL color # on the order. Contact our customer service department 
for lead times.

2 IMPORTANT: 600V and 480V models need 2 power sources (E.g.: 600V+208V or 230V) or an external transformer (E.g.: 600V/240V). The VA requirement varies between models: 
C1000 = 200VA, C1500 and C2000 = 350VA.

3 Maximum installation height when connected to 208V is 8.53 ft. (2.6 m).

- Options

| Product # | Description | ## Qty |
| --- | --- | --- |

### Others

| Type | Quantity | Model et description Complementary informations | Volts | Phase | Watts | Length mm/in. | Informations Color/installation |
| --- | --- | --- | --- | --- | --- | --- | --- |

- Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| ELectrician Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact in Ouellet: |  |
| Comments: |  |