# Series

ORA-EC40	Industrial and Commercial Air Curtain

# Features

Model	-	Electric heat.

-	No heat.

Color	-	Stainless steel housing: white (RAL 9016, NCS S 0500-N).

- 	Grille, rear face and ends: grey (RAL 7046).

-	Custom colors available upon request (RAL Chart).

Voltage	-	208V, 480V, 600V, 60 Hz.

Motor	-	Very low operating costs can be achieved thanks to the combination of EC motors and Frico's unique fan geometry.

Construction	-	External electronic board for easy connection and maintenance.

- Quick access to internal components via the maintenance hatch.

- High-limit temperature control with automatic reset.

- Integrated transformer for motor and control circuit (480V and 600V models)

Fan	-	Squirrel-cage fans.

Element	-	Element provides instant heat (electric heat model).

Control	-	SIRe control system included.

- Door switch included.

- Compatible with a Building Management System.

- Personalize programing of the air curtain.

Installation	-	Maximum height installation (horizontal mounted):

- Surface mounted: 13.1 ft. (4 m) above floor.

- Recessed: 13.1 ft. (4 m) above floor.

- Maximum width installation (vertical mounted):

- 16 to 20 ft. (5 to 6 m) 2 units, 1 on each side.

- For vertical mounting, the air curtain must be used with the joining and vertical mounting kit PA4JK (not included).

- Design kit can be used for unobtrusive installations using concealed brackets, tubes and cables (not included).

Note: The recommended installation height may vary according to the installation conditions. Air curtains must be placed as near to the entrance as possible and cover the entire width.

Warranty	-	5-year warranty against defects.

Certification	-	AMCA 210, 220 and 300 certified for performance and sound level, and meets the

following Energy Standard for Buildings Code: ANSI/ASHRAE/IES standard 90.1.

Application 	-	Garage door, vestibule, commercial building, lobby, service door, hospital, store entrance.

Models

| Product # | Qty | Volts (ph) | kW Lo/Hi | Amp. | cfm | Max velocity (ft./min)1 | dBA2 | Effective width of air stream | Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | in. | mm | lb | kg |
| Surface-mounted |
| Electric Heat |
| PAEC4010E12-600VNA |  | 600 (3) | 4/12 | 15 | 1400 | 2560 | 80 | 38 | 960 | 104 | 47 |
| PAEC4015E18-600VNA |  | 600 (3) | 6/18 | 23 | 1950 | 2560 | 81 | 58 | 1470 | 137 | 62 |
| PAEC4020E24-600VNA |  | 600 (3) | 8/24 | 30 | 2800 | 2560 | 82 | 77 | 1960 | 185 | 84 |
| PAEC4025E30-600VNA |  | 600 (3) | 10/30 | 38 | 3300 | 2560 | 83 | 97 | 2470 | 234 | 106 |
| PAEC4010E12-480VNA |  | 480 (3) | 4/12 | 18 | 1400 | 2560 | 80 | 38 | 960 | 104 | 47 |
| PAEC4015E18-480VNA |  | 480 (3) | 6/18 | 27 | 1950 | 2560 | 81 | 58 | 1470 | 137 | 62 |
| PAEC4020E24-480VNA |  | 480 (3) | 8/24 | 35 | 2800 | 2560 | 82 | 77 | 1960 | 185 | 84 |
| PAEC4025E30-480VNA |  | 480 (3) | 10/30 | 45 | 3300 | 2560 | 83 | 97 | 2470 | 234 | 106 |
| PAEC4010E10-208VNA |  | 208 (3) | 4/10 | 31 | 1400 | 2560 | 80 | 38 | 960 | 93 | 42 |
| PAEC4015E15-208VNA |  | 208 (3) | 5/15 | 45 | 1950 | 2560 | 81 | 58 | 1470 | 126 | 57 |
| PAEC4020E20-208VNA |  | 208 (3) | 7/20 | 60 | 2800 | 2560 | 82 | 77 | 1960 | 172 | 78 |
| No heat |
| PAEC4010A-NA |  | 208 (1) | - | 3.0 | 1400 | 2560 | 80 | 38 | 960 | 84 | 38 |
| PAEC4015A-NA |  | 208 (1) | - | 4.5 | 1950 | 2560 | 81 | 58 | 1470 | 108 | 49 |
| PAEC4020A-NA |  | 208 (1) | - | 6.0 | 2800 | 2560 | 82 | 77 | 1960 | 141 | 64 |
| PAEC4025A-NA |  | 208 (1) | - | 7.5 | 3300 | 2560 | 83 | 97 | 2470 | 172 | 78 |
| Recessed |
| Electric Heat |
| AREC4010E12-600VNA |  | 600 (3) | 4/12 | 15 | 1530 | 2220 | 76 | 38 | 960 | 125 | 56,5 |
| AREC4015E18-600VNA |  | 600 (3) | 6/18 | 22 | 2150 | 2220 | 76 | 59 | 1485 | 171 | 77.5 |
| AREC4020E24-600VNA |  | 600 (3) | 8/24 | 30 | 3050 | 2220 | 78 | 78 | 1975 | 224 | 101.5 |
| AREC4025E30-600VNA |  | 600 (3) | 10/30 | 36 | 3650 | 2220 | 80 | 98 | 2508 | 287 | 121.0 |
| AREC4010E12-480VNA |  | 480 (3) | 4/12 | 19 | 1530 | 2220 | 76 | 38 | 960 | 125 | 56.5 |
| AREC4015E18-480VNA |  | 480 (3) | 6/18 | 26 | 2150 | 2220 | 76 | 59 | 1485 | 171 | 77.5 |
| AREC4020E24-480VNA |  | 480 (3) | 8/24 | 35 | 3050 | 2220 | 78 | 78 | 1975 | 224 | 101.5 |
| AREC4025E30-480VNA |  | 480 (3) | 10/30 | 43 | 3650 | 2220 | 80 | 98 | 2508 | 287 | 121.0 |
| AREC4010E10-208VNA |  | 208 (3) | 4/10 | 31 | 1530 | 2220 | 76 | 38 | 960 | 117 | 53.0 |
| AREC4015E15-208VNA |  | 208 (3) | 5/15 | 44 | 2150 | 2220 | 76 | 59 | 1485 | 163 | 74.0 |
| AREC4020E20-208VNA |  | 208 (3) | 7/20 | 60 | 3050 | 2220 | 78 | 78 | 1975 | 212 | 96.0 |
| No heat |
| AREC4010A-NA |  | 208 (1) | - | 3.1 | 1530 | 2220 | 76 | 38 | 960 | 99 | 52 |
| AREC4015A-NA |  | 208 (1) | - | 3.9 | 2150 | 2220 | 76 | 59 | 1485 | 139 | 71 |
| AREC4020A-NA |  | 208 (1) | - | 6.2 | 3050 | 2220 | 78 | 78 | 1975 | 181 | 94 |
| AREC4025A-NA |  | 208 (1) | - | 7.0 | 3650 | 2220 | 80 | 98 | 2508 | 234 | 121 |

To order any custom colors from the R.A.L. chart, add “SP”’ at the end of the Product # and specify RAL color # on the order. Contact our customer service department for lead times.

1 Measurements according to AMCA 220-05. Average values for products in the series. Measurement taken at 0.3 ft. (0.1 m).

2 Values shown are for total sound power levels for Installation Type A: free inlet, free outlet. The Sound power level ratings shown are in decibels, referred to 10-12 watts, calculated per AMCA Standard 301.

# Options for horizontal mounting

| Product # | Description | Quantity included | Dimension in. | Dimension mm | Qty |
| --- | --- | --- | --- | --- | --- |
| PA34WB15 | Wall mounting brackets for 1 and 1.5 m (3.3 and 4.9 ft.) units | 2 | 16 | 400 |  |
| PA34WB20 | Wall mounting brackets for 2 m (6.6 ft.) units | 3 | 16 | 400 |  |
| PA34WB30 | Wall mounting brackets for 2.5 m (8.2 ft.) units | 4 | 16 | 400 |  |
| PA34VD15 | Vibration dampers for 1 and 1.5 m (3.3 and 4.9 ft.) units | 4 | - | - |  |
| PA34VD20 | Vibration dampers for 2 m (6.6 ft.) units | 6 | - | - |  |
| PA34VD30 | Vibration dampers for 2.5 m (8.2 ft.) units | 8 | - | - |  |
| PA4JK | Joining and vertical mounting kit PAEC4000 | 1 | - | - |  |
| PA4DW10 | Design kit for wall and vertical mounting PAEC4010x | 1 | 3 27/64 x 16 11/16 x 39 39/64 | 87 x 424 x 1006 |  |
| PA4DW15 | Design kit for wall and vertical mounting PAEC4015x | 1 | 3 27/64 x 16 11/16 x 59 11/16 | 87 x 424 x 1516 |  |
| PA4DW20 | Design kit for wall and vertical mounting PAEC4020x | 1 | 3 27/64 x 16 11/16 x 78 31/32 | 87 x 424 x 2006 |  |
| PA4DW25 | Design kit for wall and vertical mounting PAEC4025x | 1 | 3 27/64 x 16 11/16 x 99 1/16 | 87x424x2516 |  |
| PA4DCS | Design kit for ceiling mounting, small | 1 | 8 - 12 | 200 - 300 |  |
| PA4DCM | Design kit for ceiling mounting, medium | 1 | 12 - 20 | 300 - 500 |  |
| PA4DCL | Design kit for ceiling mounting, large | 1 | 20 - 36 | 500 - 900 |  |
| PA4DXT | Design kit for ceiling mounting, extension | 1 | 16 17/32 | 420 |  |

# Options for vertical mounting

| Product # | Description | Quantity included | Qty |
| --- | --- | --- | --- |
| PA4JK | Joining and vertical mounting kit PAEC4000 | 1 |  |
| PA4DW10 | Design kit for wall and vertical mounting PAEC4010x | 1 |  |
| PA4DW15 | Design kit for wall and vertical mounting PAEC4015x | 1 |  |
| PA4DW20 | Design kit for wall and vertical mounting PAEC4020x | 1 |  |
| PA4DW25 | Design kit for wall and vertical mounting PAEC4025x | 1 |  |
| AXP300 | Collision protection | 1 |  |

### Others

| Type | Quantity | Model et description Complementary informations | Volts | Phase | Watts | Length mm/in. | Informations Color/installation |
| --- | --- | --- | --- | --- | --- | --- | --- |

# Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| ELectrician Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact in Ouellet: |  |
| Comments: |