Series

OSR-NA	All Purpose Self-Regulating Heating Cable ELSR-NA

BO

BOT

AO

Features

Outer jacket	-	Thermoplastic (AO, BO) / Fluoropolymer (BOT).

Bus wire	-	Nickel plated copper, 16 AWG.

Minimum start-up

temperature	-	-30 °C (-22 °F).

Maximum operating

Temperature (power on)	-	60 °C (140 °F).

Maximum continuous

exposure temperature

(power off)	-	80 °C (176 °F).

Nominal voltage	-	120V, 240/208V.

Bending radius, min.	-	25 mm (1 in.).

Installation temperature, min.	-	AO, BO : -45 °C (-49 °F).

- BOT : -25 °C (-13 °F).

Classification	-	II 2G Ex e IIC T6 Gb  II 2D Ex tb IIIC.

-	T 80 °C Db.

-	Class I, Division 2, Groups A, B, C, D.

-	Class II, Division 2, Groups E, F, G.

-	Class III, T6.

-	Class I, Zone 1, AEx / Exe II, T6.

-	Class 1, Division 1, Groups B, C, D (Contact manufacturer).

Standards	- 	CSA C22.2.130.03; -WS.

- CAN/CSA 60079-7:12, 60079-0-11.

- ANSI/IEEE 515, 515.

Certification	- 	IECEx EPS 12.0006U.

- 12ATEX1431U.

- CSA C US 2547790.

Rating	-  Wet rated, for outdoor use (WS).

Warranty	-	1-year basic warranty on the heating cable.

Application	-	Freeze protection, heat tracing instrumentation, pipes, vessel and tanks, chemical

and petrochemical industries, food processing, automotive, roof and gutter, sprinkler systems.

Heating Circuit Length for ELSR-NA Models

| 120V |  |  |  |  |  | 240V |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Start-up temperature | CB capacity (A) | Maximum heating circuit (ft.) for |  |  |  | Start-up temperature | CB capacity (A) | Maximum heating circuit (ft.) for |  |  |  |
|  |  | ELSR-NA-3-1 | ELSR-NA-5-1 | ELSR-NA-7-1 |  |  |  | ELSR-NA-4-2 | ELSR-NA-6-2 | ELSR-NA-8-2 | ELSR-NA-10-2 |
| 10 °C (50 °F) | 10 | 159 | 125 | 82 |  | 10 °C (50 °F) | 10 | 273 | 170 | 127 | 66 |
|  | 15 | 238 | 187 | 123 |  |  | 15 | 410 | 255 | 191 | 99 |
|  | 20 | 317 | 249 | 164 |  |  | 20 | 547 | 340 | 255 | 132 |
|  | 25 | 397 | 312 | 205 |  |  | 25 | 683 | 425 | 318 | 165 |
|  | 30 | 476 | 374 | 246 |  |  | 30 | 820 | 510 | 382 | 198 |
|  | 35 | 555 | 436 | 287 |  |  | 35 | 957 | 595 | 446 | 231 |
|  | 40 | 612 | 499 | 328 |  |  | 40 | 1087 | 857 | 509 | 264 |
| 0 °C (32 °F) | 10 | 143 | 112 | 75 |  | 0 °C (32 °F) | 10 | 245 | 154 | 117 | 61 |
|  | 15 | 215 | 168 | 113 |  |  | 15 | 367 | 231 | 175 | 91 |
|  | 20 | 287 | 224 | 151 |  |  | 20 | 489 | 308 | 233 | 121 |
|  | 25 | 358 | 280 | 188 |  |  | 25 | 612 | 385 | 292 | 152 |
|  | 30 | 430 | 336 | 226 |  |  | 30 | 734 | 462 | 350 | 182 |
|  | 35 | 502 | 392 | 264 |  |  | 35 | 856 | 539 | 408 | 212 |
|  | 40 | 573 | 448 | 301 |  |  | 40 | 979 | 616 | 467 | 243 |
| -10 °C (14 °F) | 10 | 130 | 102 | 69 |  | -10 °C (14 °F) | 10 | 222 | 141 | 108 | 57 |
|  | 15 | 195 | 153 | 104 |  |  | 15 | 333 | 211 | 162 | 85 |
|  | 20 | 260 | 204 | 139 |  |  | 20 | 444 | 281 | 216 | 113 |
|  | 25 | 325 | 255 | 173 |  |  | 25 | 555 | 352 | 270 | 142 |
|  | 30 | 390 | 306 | 208 |  |  | 30 | 666 | 422 | 324 | 170 |
|  | 35 | 455 | 357 | 243 |  |  | 35 | 777 | 492 | 378 | 198 |
|  | 40 | 520 | 408 | 277 |  |  | 40 | 888 | 563 | 432 | 227 |
| -30 °C (-22 °F) | 10 | 110 | 87 | 60 |  | -30 °C (-22 °F) | 10 | 187 | 120 | 93 | 50 |
|  | 15 | 165 | 130 | 90 |  |  | 15 | 280 | 180 | 140 | 75 |
|  | 20 | 220 | 173 | 120 |  |  | 20 | 373 | 240 | 187 | 100 |
|  | 25 | 275 | 217 | 150 |  |  | 25 | 467 | 300 | 233 | 125 |
|  | 30 | 330 | 260 | 180 |  |  | 30 | 560 | 360 | 280 | 150 |
|  | 35 | 385 | 303 | 210 |  |  | 35 | 653 | 420 | 327 | 175 |
|  | 40 | 440 | 347 | 240 |  |  | 40 | 747 | 480 | 373 | 200 |

Maximum heating circuit ELSR-NA-XX on the following conditions:
• 120/240 Voltage	• MCB type QO (100% utilization)
• Voltage drop max. 10%	• Single cable fed 1 end

Eltherm® Correction Factors/Multipliers for Operation of Heating Cables in 208V

To calculate the corrected power output for operation in 208V, multiply the published output at 240V (in W/ft.) by the nominal output factor provided for the applicable heating cable type.

To calculate maximum heating circuit lengths for operation in 208V (tables provided in product data sheets), multiply the published max. heating circuit length at 240V provided for the applicable heating cable type.

| Heating Cable Correction Factors/ Multipliers | Nominal Output 208V vs. 240V | Heating Circuit Length 208V vs. 240V |
| --- | --- | --- |
| ELSR-NA-XX-2 | 0.88 | 0.93 |

Due to the cable’s self-regulating properties, the power density can reach up to 11W / ft (120V) and 13W / ft (240V) when buried in snow or ice:

"wet density".

Cable heat output depending on the environment

In Snow and Ice (120V cable)

• 11W/ft. @ 50 °F (36W/m @ 10 °C )

In Dry Air

• 7W/ft. @ 50 °F (23W/m @ 10 °C )

In Snow and Ice (240/208V cable)

• 13W/ft. @ 50 °F (42W/m @ 10 °C )

In Dry Air

• 8W/ft. @ 50 °F (26W/m @ 10 °C )

OSR Series ELSR-NA Models

| Nominal Output W/ft. | Product #1, 3 120V | Outer jacket/Mechanical shield |  |  |  |  |  | Cable dimension approx. (mm) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | AO | Qty | BO | Qty | BOT | Qty |  |
| 3 | ELSR-NA-3-1-XX |  |  |  |  |  |  | 13.8 x 5.6 |
| 5 | ELSR-NA-5-1-XX |  |  |  |  |  |  | 13.8 x 5.6 |
| 7 | ELSR-NA-7-1-XX |  |  |  |  |  |  | 14.1 x 5.6 |
| - | - | - |  | - |  | - |  | 14.1 x 5.6 |
| Nominal Output W/ft. | Product #1, 2, 3 240V | Outer jacket/Mechanical shield |  |  |  |  |  | Cable dimension approx. (mm) |
|  |  | AO | Qty | BO | Qty | BOT | Qty |  |
| 4 | ELSR-NA-4-2-XX | - |  | - |  |  |  | 13.8 x 5.6 |
| 6 | ELSR-NA-6-2-XX |  |  |  |  |  |  | 13.8 x 5.6 |
| 8 | ELSR-NA-8-2-XX |  |  |  |  |  |  | 14.1 x 5.6 |
| 10 | ELSR-NA-10-2-XX |  |  |  |  |  |  | 14.1 x 5.6 |

1  XX = Outer jacket/Mechanical shield.
  AO Aluminum foil and a thermoplastic outer jacket. 
  BO Protective braid and a thermoplastic outer jacket.
  BOT Protective braid and a fluoropolymer outer jacket.
2 For operations at 208V, please consult Correction Factors/Multipliers. 
3 When ordering, the quantity on the purchase order is equal to the length in feet of the cable required.

E.g.: To order a 500 ft., cable, write 500 for quantity with product code.

Custom cutting service available for all lengths other than 500 ft. and 1000 ft. (minimum of 25 ft.).

Options

| Product # Kit | Description | Qty |
| --- | --- | --- |
| ECA-JB1 | Junction box for single connection c/w label and fastener |  |
| ECA-JB2 | Junction box for double connection c/w label and fastener |  |
| EL-CLIC-P | Quick connector with supply lead, for 1 to 3 cables |  |
| EL-CLIC-S | Quick connector for direct connection or cold lead connection of 1 to 3 cables |  |
| EL-ECN-EX1 | End termination for ELSR-NA |  |
| EL-SPN-16 | Heat shrink splice-kit suitable for ELSR-NA and cold lead connections |  |
| ELAK-3-7 | Junction box with mounting stand for non-hazardous (ordinary) and hazardous locations |  |
| ELVB-SRAN | Power connection without cable gland |  |
| ELVB-SRAN-12-PA | Power connection with plastique/PA12 cable gland/fitting, 1/2'' NPT, non-hazardous location |  |
| ELVB-SRAN-34-PA | Power connection with plastique/PA12 cable gland/fitting, 3/4'' NPT, non-hazardous location |  |
| ELVB-SRAN-34-ST | Power connection with steel/zinc cable gland/fitting, 3/4'' NPT, non-hazardous location |  |
| ELVB-SREX-34-HT1 | Power connection with nickel plated cable gland, 3/4'' NPT, hazardous location |  |
| ELVB-SREX-M20-HT1 | Power connection with nickel plated cable gland, M20, hazardous location |  |
| KIT-OSR-ELSR-NA | End and power termination kit with warning sticker NA Series |  |
| KIT-OSR-DRD-120V | Roof drain de-icing kit with 50’ of 120V 7w/ft. OSR-NA cable (ELSR-NA-7-1-BO) |  |
| KIT-OSR-DRD-240V | Roof drain de-icing kit with 50’ of 240V 8w/ft. OSR-NA cable (ELSR-NA-8-2-BO) |  |
| Multiple applications |  |  |
| KIT-OSR-EL-WS03 | Warning label/sign bilingual (English / French) |  |
| Roof and gutter |  |  |
| ELB-20 | Downspout 90° mounting plate |  |
| ELB-21 | Gutter mounting plate |  |
| ELB-RCLIP | Roof clips for cable, qty 25 |  |
| Pipe tracing |  |  |
| ELB-02B | Self-adhesive glass fiber tape, max. temp. = 90 °C (194 °F), 50 m (165 ft.) |  |
| ELB-06C | Self-adhesive aluminum tape, max. temp. = 80 °C (176 °F), 50 m (165 ft.) |  |

1 Minimum installation temperature -45 °C (-49 °F).

Controls

| Product # | Description | Qty |
| --- | --- | --- |
| Controller options for roof and gutter for de-icing |  |  |
| DS-2C1 | Aerial mounted controller with sensor to detect humidity and temperature, 30A, 100V to 277V |  |
| DS-8C1 | Aerial mounted controller with sensor to detect temperature and a sensor to detect humidity with 10 ft. (3 m) cable, 30A, 100V to 277V |  |
| DS-9C1 | Aerial mounted controller with sensor to detect temperature and a sensor to detect humidity with 10 ft. (3 m) cable, 2 X 30A, 100V to 277V |  |
| EX-50 | 50 ft. (15 m) extension kit, with connection fittings for humidity sensor |  |
| CDP-2 | Interior controller and display for DS products |  |
| ETO21 | Dual-zone electronic controller, 3 X 16A, 120V to 240V |  |
| ETF-744/99 | 24V outdoor sensor for measuring temperature |  |
| ETOR-55 | Gutter sensor to detect humidity with 33 ft. (10 m) cable |  |
| Controller options for pipe tracing for use in non-hazardous (ordinary) locations |  |  |
| ECA-E55-R25HT1 | SPDT, NEMA 4X thermostat in molded aluminum housing, 22A at 120/250/480V, with 10 ft. (3 m) stainless steel bulb and capillary |  |
| TPR-L1N-3X-Q101 | SPDT, NEMA 4X thermostat in polycarbonate housing, 22A at 120/250/480V, with 3 ft. (1 m) tinned copper bulb and capillary |  |
| TPR-L1N-10X-Q101 | SPDT, NEMA 4X thermostat in polycarbonate housing, 22A at 120/250/480V, with 10 ft. (3 m) tinned copper bulb and capillary |  |
| TRF115-0051 | SPDT, NEMA 4X thermostat, range -17 °C to 49 °C (0 °F to 120 °F), 25A at 120/208/240/277V, with 5 ft. (1.5 m) stainless bulb and capillary |  |
| TRF115-0071 | SPDT, NEMA 4X thermostat, range -35 °C to 38 °C (-30 °F to 100 °F), 25A at 120/208/240/277V, with 8 ft. (2.4 m) copper bulb and capillary |  |
| ELTC-14-RTD1 | Digital temperature control 20A at 90-260V, including 3-wire RTD (Pt-100) sensing element is 5x50mm with 5m of fluoropolymer lead wires, range 0 to 250°C |  |
| GPT-130 | Single point heat trace control thermostat NEMA 4X c/w GFEP and a 20 ft. thermistor 30A@100-277V |  |
| S1-A | NEMA 4X IP67 electronic single point line sensing heat trace controller 100-277V, 30A c/w built-in 30 mA GFEP and 20' (6 m) lead, 10k ohms thermistor, Wi-Fi, Ethernet, Modbus and BACnet3 capabilities |  |
| S1-B | NEMA 4X IP67 electronic single point line sensing heat trace controller 100-277V, 30A c/w built-in 30 mA GFEP and 20' (6 m) lead, 10k ohms thermistor, Wi-Fi, Ethernet |  |
| GATEWAY-PCKG | 24VDC BACnet gateway assembly with power supply NEMA 4X enclosure with 24VDC transformer for S1 Series |  |
| GATEWAY | 24VDC BACnet gateway stand alone for S1 Series |  |
| Controller options for pipe tracing for use in non-hazardous (ordinary) and hazardous locations |  |  |
| TXR-L2S-10-Q101 | SPDT, explosion-proof, NEMA 4, 7 and 9 thermostat, in anodized aluminum housing, 22A at 120/250/480V, with 10 ft. (3 m) stainless steel bulb and capillary |  |
| TM-1SIH1-E5-RTD-A1 | TraceMateTM I GFCI electronic thermostat for single circuit at 120V |  |
| TM-1DIH2-E5-RTD-A1 | TraceMateTM I GFCI electronic thermostat for single circuit at 240/208V |  |
| TM-2SIH1-E5-RTD | TraceMateTM II GFCI electronic thermostat for dual circuit at 120V |  |
| TM-2DIH2-E5-RTD | TraceMateTM II GFCI electronic thermostat for dual circuit at 240/208V |  |
| MS-21012 | MasterTrace Single circuit electronic GFCI controller with double pole, 85V to 280V, 30A, with user interface |  |
| MS-21022 | MasterTrace Double circuit electronic GFCI controller with single pole, 120V or 277V, 30A, with user interface |  |
| RTD-7 | RTD probe for MasterTrace controller |  |
| Control panel options |  |  |
| SR-4CIR-240 | 4 circuits 240V 30A circuit GFEP control panel with contactors and 240-120V control transformer (HxWxD: 20x16x8 in.) |  |
| SR-6CIR-240 | 6 circuits 240V 30A circuit GFEP control panel with contactors and 240-120V control transformer (HxWxD: 20x16x8 in.) |  |
| SR-8CIR-240 | 8 circuits 240V 30A circuit GFEP control panel with contactors and 240-120V control transformer (HxWxD: 24x20x8 in.) |  |
| SR-12CIR-240 | 12 circuits 240V 30A circuit GFEP control panel with contactors and 240-120V control transformer (HxWxD: 24x24x8 in.) |  |

1 Requires a ground fault circuit interrupter (GFCI) in the electrical panel.

2 Requires a RTD probe for MasterTrace controller (RTD-7).

3 BACnet IP or MS/TP available via preconfigured SMC gateway, sold separately.

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electricial Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact in Ouellet: |  |
| Comments: |  |