Series

OTP-E	Eagle Ductless Single Zone Heat Pump

Features

Operation mode	- 	Cooling, heating, dehumidifying, fan and auto.

Nominal capacity	-	9000, 12000, 18000, 24000 BTU/hr.

Voltage	-	230/208V, 60 Hz, 1-phase.

Indoor unit	- 	High wall installation, dual side connection.

-	Plastic housing, standard white.

-	4-speed cross-flow fan (auto, high, medium and low).

-	Washable filters.

Outdoor unit	-	Variable speed rotary compressor (INVERTER), with overload protection.

-	Electronic expansion valve for precise control of refrigerant flow.

-	Condenser fins covered with a hydrophilic coating for improved corrosion resistance.

-	Large diameter quiet axial-flow fan for more efficient heat exchange.

-	Smart pan heater to prevent ice formation.

-	Installation on aluminum wall bracket or ground stand (optional).

Connection piping	-	Minimum piping length of 10 ft. (3 m).

- External liquid pipe diameter: 1/4”.

- External gas pipe diameter: 3/8” to 5/8”.

- Flared connections.

Control 	-	Wireless remote included.

-	Wired wall controller available.

-	Wi-Fi capability (option KIT-WIFI required).
-	Interface (options HP6000ZB-GE and GT130 required).

-	Set temperature: 16 to 30 °C (61 to 86 °F).

-	Temperature display format: °C or °F.

Warranty	- 10-year basic warranty on parts and 10-year basic warranty on the compressor (labour not included).

Application	-	Dining room-kitchen, living room, family room, commercial building, office building, condo, restaurant.

Models

| Product #1 |  |  | Indoor Unit |  |  | SED09KCH17S-I SED09KCH17S-O | SED12KCH17S-I SED12KCH17S-O | SED18KCH16S-I SED18KCH16S-O | SED24KCH19S-I SED24KCH19S-O |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Outdoor Unit |  |  |  |  |  |  |
| Qty |  |  |  |  |  |  |  |  |  |
| Technical Performance |  |  |  |  |  |  |  |  |  |
| Voltage |  |  |  |  | Volts | 230/208 | 230/208 | 230/208 | 230/208 |
| Cooling capacity |  | Nominal |  |  | W (BTU/hr) | 2667 (9100) | 3517 (12000) | 5100 (17400) | 6450 (22000) |
|  |  | Min. – max. |  |  | W (BTU/hr) | 720 - 2814 (2457 - 9600) | 300 - 3700 (1024 - 12624) | 1200 - 5800 (4094 - 20000) | 1730 - 7400 (5900 - 25200) |
| Heating capacity |  | Nominal |  |  | W (BTU/hr) | 2784 (9500) | 3810 (13000) | 5275 (18000) | 7034 (24000) |
|  |  | Min. – max. |  |  | W (BTU/hr) | 720 – 3371 (2457 - 11500) | 700 - 4000 (2388 - 13648) | 1200 – 6200 (4100 - 21000) | 1310 - 7600 (4500 - 25900) |
| Used cooling power input |  | Nominal |  |  | W | 889 | 1297 | 2040 | 1950 |
|  |  | Min. – max. |  |  | W | 185 - 1100 | 180 - 1500 | 200 - 2300 | 360 - 3000 |
| Used heating power input |  | Nominal |  |  | W | 774 | 1172 | 1758 | 2070 |
|  |  | Min. – max. |  |  | W | 170-1350 | 260 - 1450 | 300 - 2400 | 330 - 2900 |
| Used rated input |  |  |  |  | W | 1350 | 1500 | 2400 | 2900 |
| Rated current |  |  |  |  | A | 6.3 | 6.5 | 10 | 11 |
| MCA |  |  |  |  | A | 10 | 9 | 15 | 19 |
| Max. over-current protection (MOCP) |  |  |  |  | A | 15 | 15 | 20 | 30 |
| SEER |  |  |  |  | - | 17 | 17 | 16 | 19 |
| HSPF |  |  |  |  | - | 9 | 9 | 9 | 10 |
| EER |  |  |  |  | W/W | 3 | 2.71 | 2.5 | 3.31 |
| COP |  |  |  |  | W/W | 3.6 | 3.25 | 3 | 3.4 |
| AHRI number |  |  |  |  | - | 205782700 | 205782701 | 205782702 | 205782703 |
| Indoor Unit |  |  |  |  |  |  |  |  |  |
| Dehumidification |  |  |  | pt/hr (l/hr) |  | 1.69 (0.80) | 2.96 (1.4) | 3.8 (1.80) | 4.23 (2.00) |
| Air flow volume |  | T / H / M / L2 |  | cfm |  | 294 / 271 / 235 / 182 | 371 / 294 / 235 / 182 | 471 / 412 / 383 / 335 | 677 / 588 / 471 / 412 |
| Sound level |  | T / H / M / L2 |  | dB (A) |  | 49 / 47 / 43 / 36 | 52 / 49 / 44 / 38 | 57 / 54 / 50 / 45 | 59 / 55 / 51 / 47 |
| Fan motor power output |  |  |  | W |  | 20 | 20 | 60 | 30 |
| Fan motor RLA |  |  |  | A |  | 0.22 | 0.31 | 0.4 | 0.55 |
| Deflector stepper motor power output |  |  |  | W |  | 1.5 | 1.5 | 2.5 | 2.5 |
| Net weight |  |  |  | lb (kg) |  | 19.8 (9) | 22 (10) | 30 (13.5) | 37.5 (17) |
| Outdoor Unit |  |  |  |  |  |  |  |  |  |
| Air flow volume |  |  |  | cfm |  | - | - | - | - |
| Sound level |  |  |  | dB (A) |  | 60 | 60 | 66 | 69 |
| Compressor power input |  |  |  | W |  | 790 | 1023 | 1440 | 1635 |
| Compressor LRA |  |  |  | A |  | 18 | 18 | 25 | 25 |
| Compressor RLA |  |  |  | A |  | 6.6 | 6.6 | 10.2 | 13 |
| Fan motor power output |  |  |  | W |  | 30 | 30 | 60 | 60 |
| Fan motor RLA |  |  |  | A |  | 0.37 | 0.37 | 0.7 | 0.65 |
| Refrigerant volume (R410A) |  |  |  | oz (g) |  | 24 (680) | 28.2 (800) | 42.3 (1200) | 52.9 (1500) |
| Net weight |  |  |  | lb (kg) |  | 58.4 (26.5) | 63 (28.5) | 87 (39.5) | 97 (44) |
| Operating ambient temperature | Cooling |  |  | °C (°F) |  | -18 to 46 (0 to 115) |  |  |  |
|  | Heating |  |  | °C (°F) |  | -20 to 24 (-4 to 75) |  |  |  |
| Connection Piping/Refrigerant |  |  |  |  |  |  |  |  |  |
| Pre-charge length |  |  |  | ft. (m) |  | 25 (7.5) | 25 (7.5) | 25 (7.5) | 25 (7.5) |
| Additional refrigerant charge |  |  |  | oz/ft. (g/m) |  | 0.2 (20) | 0.2 (20) | 0.2 (20) | 0.5 (50) |
| Liquid pipe outer diameter |  |  |  | in. |  | 1/4 | 1/4 | 1/4 | 1/4 |
| Gas pipe outer diameter |  |  |  | in. |  | 3/8 | 3/8 | 1/2 | 5/8 |
| Maximum height difference |  |  |  | ft. (m) |  | 33 (10) | 33 (10) | 33 (10) | 33 (10) |
| Maximum total length |  |  |  | ft. (m) |  | 49 (15) | 66 (20) | 82 (25) | 82 (25) |

1 1 indoor unit and 1 outdoor unit. Note that each unit is individually packaged.

2 Cross-Flow Fan Speeds: (T) Turbo / (H) High / (M) Medium / (L) Low.

Capacity Variation Ratio According to Temperature

SED09

SED12

SED18

SED24

| Indoor Unit | L |  | H |  | D |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm |
| SED09KCH17S-I | 31 1/8 | 790 | 10 13/16 | 275 | 7 7/8 | 200 |
| SED12KCH17S-I | 33 1/4 | 845 | 11 3/8 | 289 | 7 7/8 | 209 |
| SED18KCH16S-I | 38 3/16 | 970 | 11 13/16 | 300 | 8 13/16 | 224 |
| SED24KCH19S-I | 42 7/16 | 1078 | 12 13/16 | 325 | 9 11/16 | 246 |

| Outdoor Unit | L |  | H |  | D |  | A |  | B |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| SED09KCH17S-O | 30 13/16 | 782 | 21 1/4 | 540 | 12 5/8 | 320 | 21 1/4 | 540 | 11 1/4 | 286 |
| SED12KCH17S-O | 30 13/16 | 782 | 21 1/4 | 540 | 12 5/8 | 320 | 21 1/4 | 540 | 11 1/4 | 286 |
| SED18KCH16S-O | 35 15/16 | 912 | 25 7/16 | 646 | 14 11/16 | 373 | 22 | 559 | 14 5/16 | 364 |
| SED24KCH19S-O | 38 9/16 | 980 | 31 1/8 | 790 | 16 13/16 | 427 | 24 | 610 | 15 9/16 | 395 |

Options
See OTP Options section

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrical Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact at Ouellet: |  |
| Comments: |  |