Series

OTP-H	Harmony Ductless Single Zone Heat Pump

Features

Operation mode	- 	Cooling, heating, dehumidifying, fan and auto.

Nominal capacity	-	9000, 12000, 18000, 24000 BTU/hr.

Voltage	-	230/208V, 60 Hz, 1-phase.

Indoor unit	- 	High wall installation, dual side connection.

-	Plastic housing, standard white.

-	7-speed cross-flow fan (auto, turbo, high, medium-high, medium, low and very low).

-	Washable filters.

Outdoor unit	-	Variable speed rotary compressor (INVERTER), with overload protection.

-	Electronic expansion valve for precise control of refrigerant flow.

-	Condenser fins covered with a hydrophilic coating for improved corrosion resistance.

-	Large diameter quiet axial-flow fan for more efficient heat exchange.

-	Smart pan heater to prevent ice formation.

-	Compressor blanket and preheating technology.

-		Installation on aluminum wall bracket or ground stand (optional).

Connection piping	-	Minimum piping length of 10 ft. (3 m).

- Flared connections.

Control 	-	Wireless remote included.

-	Wired wall controller available.

-	Wi-Fi.

-	Set temperature: 16 to 30 °C (61 to 86 °F).

-	Temperature display format: °C or °F.

Warranty	- 10-year basic warranty on parts and 10-year basic warranty on the compressor (labour not included).

- Labour warranty (sold separately) from the 1st to 10th year, on parts and labour with system replacement if the compressor fails.

Application	-	Dining room-kitchen, living room, family room, commercial building, office building, condo, restaurant.

Models

| Product #1 |  |  | Indoor Unit |  |  | CHD09KCH19S-I CHD09KCH19S-O | CHD12KCH17S-I CHD12KCH17S-O | CHD18KCH17S-I CHD18KCH17S-O | CHD24KCH18S-I CHD24KCH18S-O |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Outdoor Unit |  |  |  |  |  |  |
| Qty |  |  |  |  |  |  |  |  |  |
| Technical Performance |  |  |  |  |  |  |  |  |  |
| Voltage |  |  |  |  | Volts | 230/208 | 230/208 | 230/208 | 230/208 |
| Cooling capacity |  | Nominal |  |  | W (BTU/hr) | 2667 (9100) | 3517 (12000) | 5159 (17600) | 6450 (22000) |
|  |  | Min. – max. |  |  | W (BTU/hr) | 820 - 3018 (2800 - 10300) | 700 - 3700 (2388 - 13307) | 1100 - 5850 (3753 - 19960) | 2000 - 7400 (6824 - 25249) |
| Heating capacity |  | Nominal |  |  | W (BTU/hr) | 2931 (10000) | 3517 (12000) | 5598 (19100) | 7040 (24000) |
|  |  | Min. – max. |  |  | W (BTU/hr) | 655 - 3575 (2200 - 12200) | 700 - 4400 (2388 - 15013) | 800 - 6600 (2730 - 22519) | 1750 - 8000 (5971 - 27296) |
| Used cooling power input |  | Nominal |  |  | W | 805 | 1334 | 1750 | 1896 |
|  |  | Min. – max. |  |  | W | 180 - 1350 | 180 - 1500 | 200 - 2300 | 340 - 2350 |
| Used heating power input |  | Nominal |  |  | W | 781 | 1004 | 1750 | 2051 |
|  |  | Min. – max. |  |  | W | 150 -1450 | 260 - 1650 | 260 - 2300 | 370 - 2400 |
| Used rated input |  |  |  |  | W | 1450 | 1650 | 2300 | 2400 |
| Rated current |  |  |  |  | A | 6.5 | 6.7 | 9.5 | 12 |
| MCA |  |  |  |  | A | 9 | 11 | 14 | 15 |
| Max. over-current protection (MOCP) |  |  |  |  | A | 15 | 15 | 20 | 20 |
| SEER2 (SEER) |  |  |  |  | - | 19.5 (19.5) | 17.5 (17.5) | 17.5 (17.5) | 18 (18) |
| HSPF2 (HSPF) |  |  |  |  | - | 8.8 (10) | 8.5 (10) | 8.5 (9) | 8.5 (10) |
| EER |  |  |  |  | W/W | 3.30 | 2.64 | 2.95 | 3.40 |
| COP |  |  |  |  | W/W | 3.75 | 3.50 | 3.20 | 3.43 |
| AHRI number |  |  |  |  | - | 210410121 | 210410122 | 210410123 | 210410124 |
| ENERGY STAR |  |  |  |  | - | - | - | - | - |
| Indoor Unit |  |  |  |  |  |  |  |  |  |
| Dehumidification |  |  |  | pt/hr (l/hr) |  | 1.69 (0.80) | 2.96 (1.40) | 3.8 (1.80) | 5.28 (2.50) |
| Air flow volume |  |  |  | cfm |  | 353 / 282.5 / 264.8 / 229.5 / 211.86 / 194.2 / 158.8 | 424 / 353 / 324 / 277 / 247 / 224 / 182 | 618 / 512 / 471 / 436 / 395 / 336 / 283 | 677 / 588 / 559 / 500 / 471 / 441 / 412 |
| Sound level |  |  |  | dB (A) |  | 51 / 47 / 44 / 42 / 41 / 38 / 36 | 57 / 49 / 48 / 45 / 43 / 42 / 37 | 60 / 56 / 54 / 52 / 50 / 46 / 42 | 61 / 57 / 55 / 52 / 50 / 48 / 46 |
| Fan motor power output |  |  |  | W |  | 20 | 15 | 45 | 60 |
| Fan motor RLA |  |  |  | A |  | 0.30 | 0.40 | 0.70 | 0.45 |
| Deflector stepper motor power output |  |  |  | W |  | 1.5 | 1.5 | 2.5 | 2.5 |
| Net weight |  |  |  | lb (kg) |  | 19.8 (9) | 19.8 (9) | 28.7 (13) | 33 (18) |
| Outdoor Unit |  |  |  |  |  |  |  |  |  |
| Air flow volume |  |  |  | m3/hr |  | 1950 | 1950 | 2520 | 3200 |
| Sound level |  |  |  | dB (A) |  | 51 | 52 | 57 | 57 |
| Compressor power input |  |  |  | W |  | 756 | 587 | 1295 | 1330 |
| Compressor LRA |  |  |  | A |  | - | - | 25 | 35 |
| Compressor RLA |  |  |  | A |  | 5.20 | 7.30 | 9.35 | 10.45 |
| Fan motor power output |  |  |  | W |  | 30 | 30 | 30 | 60 |
| Fan motor RLA |  |  |  | A |  | 0.4 | 0.6 | 0.9 | 0.6 |
| Refrigerant volume (R410A) |  |  |  | oz (g) |  | 24.7 (700) | 27.5 (750) | 44.1 (1150) | 52.9 (1500) |
| Net weight |  |  |  | lb (kg) |  | 56.22 (25.5) | 57.33 (26) | 71.70 (32.5) | 97 (44) |
| Operating ambient temperature | Cooling |  |  | °C (°F) |  | -18 to 46 (0 to 115) |  |  |  |
|  | Heating |  |  | °C (°F) |  | -20 to 24 (-4 to 75) |  |  |  |
| Connection Piping/Refrigerant |  |  |  |  |  |  |  |  |  |
| Pre-charge length |  |  |  | ft. (m) |  | 25 (7.5) | 25 (7.5) | 25 (7.5) | 25 (7.5) |
| Additional refrigerant charge |  |  |  | oz/ft. (g/m) |  | 0.2 (20) | 0.2 (20) | 0.2 (20) | 0.5 (50) |
| Liquid pipe outer diameter |  |  |  | in. |  | 1/4 | 1/4 | 1/4 | 1/4 |
| Gas pipe outer diameter |  |  |  | in. |  | 3/8 | 3/8 | 1/2 | 5/8 |
| Maximum height difference |  |  |  | ft. (m) |  | 40 (12.2) | 40 (12.2) | 66 (20) | 82 (25) |
| Maximum total length |  |  |  | ft. (m) |  | 66 (20) | 66 (20) | 82 (25) | 131 (40) |

1 1 indoor unit and 1 outdoor unit. Note that each unit is individually packaged

Capacity Variation Ratio According to Temperature

| Indoor Unit | L |  | H |  | D |  | A |  | B |  | C |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| CHD09KCH19S-I CHD12KCH17S-I | 32 7/8 | 835 | 10 7/8 | 275 | 7 7/8 | 200 | 7 1/16 | 119 | 18 5/32 | 542 | 7 11/16 | 184 |
| CHD18KCH17S-I | 37 1/8 | 943 | 13 1/8 | 333 | 9 11/16 | 246 | 7 17/32 | 102 | 22 1/16 | 686 | 7 1/2 | 183 |
| CHD24KCH18S-I | 42 7/16 | 1078 | 13 1/8 | 333 | 9 11/16 | 246 | 10 3/16 | 206 | 22 1/16 | 686 | 10 5/32 | 186 |

| Outdoor Unit | L |  | H |  | D |  | A |  | B |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | in. | mm | in. | mm | in. |
| CHD09KCH19S-O CHD12KCH17S-O | 28 13/16 | 732 | 21 54/64 | 555 | 13 | 330 | 17 15/16 | 540 | 12 3/16 | 286 |
| CHD18KCH17S-O | 31 37/64 | 802 | 21 54/64 | 555 | 13 50/64 | 350 | 20 5/32 | 559 | 13 2/32 | 364 |
| CHD24KCH18S-O | 37 3/4 | 958 | 26 | 660 | 15 53/64 | 402 | 22 13/32 | 610 | 14 19/32 | 395 |

Options
See OTP Options section

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrical Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact at Ouellet: |  |
| Comments: |  |