Series

OTP-P	Pacific Ductless Single Zone Heat Pump

Features

Operation mode	- 	Cooling, heating, dehumidifying, fan and auto.

Nominal capacity	-	9000, 12000, 18000, 24000 BTU/hr.

Voltage	-	230/208V, 60 Hz, 1-phase.

Indoor unit	- 	High wall installation, dual side connection.

-	Plastic housing, standard white.

-	7-speed cross-flow fan (auto, turbo, high, medium-high, medium, low and very low).

-	Washable filters.

Outdoor unit	-	Variable speed rotary compressor (INVERTER), with overload protection.

-	Electronic expansion valve for precise control of refrigerant flow.

-	Condenser fins covered with a hydrophilic coating for improved corrosion resistance.

-	Large diameter quiet axial-flow fan for more efficient heat exchange.

-	Smart pan heater to prevent ice formation.

-	Compressor blanket and preheating technology.

-		Installation on aluminum wall bracket or ground stand (optional).

Connection piping	-	Minimum piping length of 10 ft. (3 m).

- Flared connections.

Control 	-	Wireless remote included.

-	Wired wall controller available.

-	Wi-Fi in option.

-	Set temperature: 16 to 30 °C (61 to 86 °F).

-	Temperature display format: °C or °F.

Warranty	- 10-year basic warranty on parts and 10-year basic warranty on the compressor (labour not included).

- Labour warranty (sold separately) from the 1st to 10th year, on parts and labour with system replacement if the compressor fails.

Application	-	Dining room-kitchen, living room, family room, commercial building, office building, condo, restaurant.

Models

| Product #1 | Indoor Unit | PUD09KCH25S-I PUD09KCH25S-O | PUD12KCH24S-I PUD12KCH24S-O | PUD18KCH23S-I PUD18KCH23S-O | PUD24KCH24S-I PUD24KCH24S-O |
| --- | --- | --- | --- | --- | --- |
|  | Outdoor Unit |  |  |  |  |
| Qty |  |  |  |  |
| Technical Performance |
| Voltage |  | Volts | 230/208 | 230/208 | 230/208 | 230/208 |
| Cooling capacity | Nominal | W (BTU/hr) | 2667 (9100) | 3517 (12000) | 5275 (18000) | 6450 (22000) |
|  | Min. – max. | W (BTU/hr) | 450 - 3150 (1535 - 10748) | 900 - 4132 (3070 - 14100) | 1500 - 6200 (5118 - 21154) | 2600 - 8200 (8870 - 28000) |
| Heating capacity | Nominal | W (BTU/hr) | 3077 (10500) | 3517 (12000) | 5275 (18000) | 7040 (24000) |
|  | Min. – max. | W (BTU/hr) | 1000 - 4300 (3412 - 14671) | 900 - 4543 (3071 - 15500) | 1500 - 6200 (5118 - 21154) | 2100 - 9000 (7200 - 30708) |
| Used cooling power input | Nominal | W | 619 | 961 | 1384 | 1679 |
|  | Min. – max. | W | 130 - 1013 | 220 - 1400 | 130 - 2300 | 290 - 2600 |
| Used heating power input | Nominal | W | 848 | 923 | 1384 | 1870 |
|  | Min. – max. | W | 228 -1343 | 220 - 1500 | 250 - 2350 | 470 - 3100 |
| Used rated input | W | 1343 | 1500 | 2350 | 3100 |
| Rated current | A | 4.73 | 6.30 | 11.50 | 15.30 |
| MCA | A | 10 | 10 | 14 | 16 |
| Max. over-current protection (MOCP) | A | 15 | 15 | 20 | 25 |
| SEER2 (SEER) | - | 25.5 (25.5) | 24 (24) | 23.5 (23) | 24.5 (24) |
| HSPF2 (HSPF) | - | 10.2 (12) | 9 (11) | 9 (11) | 9.5 (11) |
| EER | W/W | 4.31 | 3.66 | 3.81 | 3.85 |
| COP | W/W | 3.90 | 3.81 | 3.81 | 3.79 |
| AHRI number | - | 210534142 | 210534143 | 211619266 | 210534144 |
| ENERGY STAR | - | ( | ( | ( | ( |
| Indoor Unit |  |  |  |  |
| Dehumidification | pt/hr (l/hr) | 1.69 (0.80) | 2.96 (1.4) | 3.80 (1.8) | 5 (2.40) |
| Air flow volume |  | cfm | 353 / 323 / 294 / 264 / 235 / 176 / 158 | 400 / 364 / 329 / 288 / 264 / 247 / 229 | 589 / 500 / 441 / 412 / 383 / 353 / 324 | 736 / 588 / 530 / 471 / 441 / 412 / 383 |
| Sound level |  | dB (A) | 50 / 47 / 45 / 42 / 39 / 36 / 35 | 53 / 48 / 46 / 44 / 42 / 40 / 37 | 59 / 53 / 51 / 50 / 47 / 43 / 39 | 62 / 54 / 52 / 49 / 48 / 46 / 44 |
| Fan motor power output | W | 15 | 15 | 45 | 60 |
| Fan motor RLA | A | 0.22 | 0.20 | 0.35 | 0.30 |
| Deflector stepper motor power output | W | 1.5 | 1.5 | 1.5 | 1.5 |
| Net weight | lb (kg) | 21 (9.5) | 21 (9.5) | 29 (13.5) | 35 (16) |
| Outdoor Unit |  |  |  |  |
| Air flow volume | m3/hr | 2200 | 2200 | 3600 | 4500 |
| Sound level | dB (A) | 52 | 52 | 59 | 62 |
| Compressor power input | W | 800 | 784 | 1196 | 1350 |
| Compressor LRA | A | - | - | - | - |
| Compressor RLA | A | 6.50 | 6.80 | 9.25 | 11 |
| Fan motor power output | W | 30 | 30 | 60 | 90 |
| Fan motor RLA | A | 0.4 | 0.4 | 0.9 | 0.6 |
| Refrigerant volume (R410A) | oz (g) | 35.28 (1000) | 42.33 (1200) | 54.70 (1550) | 60 (1700) |
| Net weight | lb (kg) | 70.5 (32) | 70.5 (32) | 98 (44.5) | 108 (49) |
| Operating ambient temperature | Cooling | °C (°F) | -29 to 50 (-20 to 122) |
|  | Heating | °C (°F) | -30 to 30 (-22 to 86) |
| Connection Piping/Refrigerant |
| Pre-charge length | ft. (m) | 25 (7.5) | 25 (7.5) | 25 (7.5) | 25 (7.5) |
| Additional refrigerant charge | oz/ft. (g/m) | 0.2 (20) | 0.2 (20) | 0.5 (50) | 0.5 (50) |
| Liquid pipe outer diameter | in. | 1/4 | 1/4 | 1/4 | 1/4 |
| Gas pipe outer diameter | in. | 3/8 | 1/2 | 5/8 | 5/8 |
| Maximum height difference | ft. (m) | 40 (12.2) | 40 (12.2) | 66 (20) | 82 (25) |
| Maximum total length | ft. (m) | 66 (20) | 66 (20) | 82 (25) | 131 (40) |

1 1 indoor unit and 1 outdoor unit. Note that each unit is individually packaged

Capacity Variation Ratio According to Temperature

| Indoor Unit | L | H | D | A | B | C |
| --- | --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm | in. | mm |
| PUD09KCH25S-I PUD12KCH24S-I | 32 1/2 | 825 | 11 1/2 | 293 | 7 23/32 | 196 | 5 7/8 | 149 | 21 5/16 | 542 | 8 1/32 | 204 |
| PUD18KCH23S-I | 39 3/16 | 995 | 12 1/4 | 311 | 8 11/16 | 221 | 8 1/2 | 203 | 27 | 686 | 9 1/4 | 235 |
| PUD24KCH24S-I | 43 1/2 | 1105 | 13 7/64 | 333 | 9 11/16 | 246 | 8 1/2 | 203 | 27 | 686 | 9 1/4 | 235 |

| Outdoor Unit | L | H | D | A | B |
| --- | --- | --- | --- | --- | --- |
|  | in. | mm | in. | mm | in. | in. | mm | in. | mm | in. |
| PUD09KCH25S-O PUD12KCH24S-O | 31 37/64 | 802 | 21 54/64 | 555 | 13 50/64 | 350 | 20 5/32 | 512 | 13 5/64 | 332 |
| PUD18KCH23S-O | 37 46/64 | 958 | 26 | 660 | 15 53/64 | 402 | 24 | 610 | 15 9/16 | 395 |
| PUD24KCH24S-O | 39 6/16 | 1000 | 29 6/16 | 746 | 16 13/16 | 427 | 24 | 610 | 15 9/16 | 395 |

Options
See OTP Options section

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrical Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact at Ouellet: |  |
| Comments: |