Series

OTS	Trench insert floor convector

Features

Color	-	Standard: semi-gloss black.

-	Optional (upcharge applicable): white, almond, metallic silver, bronze, metallic 
charcoal, aluminum, sand.

-	Custom colors available upon request.

Finish	-	Standard: epoxy/polyester powder paint.

Voltage	-	120V, 208V, 240/208V, 277V, 347V, 480V, 600V, 1-phase.

Construction	-	Sturdy construction of 20-gauge steel.

-	Linear high-limit temperature control with automatic reset.

-	Linear high-limit temperature control with manual reset.

Heating element	-	Stainless steel tubular heating element with aluminum fins.

-	Floating heating element on high-temperature nylon bushings 
reducing expansion noises.

Watt density	-	Average standard watt density of 250W/ft.

- Average low density of 200W/ft., 167W/ft.

Control	-	Mechanical or electronic relays available (installed on the right end only).

Ouellet highly recommends using an electronic wall thermostat for greater comfort.

Installation	-	Must be installed inside a trench under a floor with a compatible top trench grille 
(not supplied), which must cover the entire length of the heater. Please refer to the table of Models of compatible top trench grilles.

- 2 fixing holes in the bottom of the heater.

Warranty	-	3-year warranty against defects.

-	10-year warranty on the heating element.

Application 	-	Bay window, lobby, commercial building, condos, restaurants.

| Models of compatible top trench grilles |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Trench dimension - Figure 3 |  |  |  |  |  |
|  |  | W: 10 in. (254 mm) minimum D: 6 in. to 7 15/16 in. (153 mm à 202 mm) C: 2 1/2 in. (64 mm) minimum |  |  | W: 10 in. (254 mm) minimum D: 8 in. (204 mm) minimum C: 2 1/2 in. (64 mm) minimum |  |  |
|  |  | Power per linear foot |  |  | Power per linear foot |  |  |
| Manufacturer | Grille Model | 167W/ft. | 200W/ft. | 250W/ft. | 167W/ft. | 200W/ft. | 250W/ft. |
| Nailor Industries www.nailor.com | 49-240 | √ | ₋ | ₋ | √ | √ | ₋ |
|  | 49-241 | √ | ₋ | ₋ | √ | √ | ₋ |
|  | 49-243 | √ | ₋ | ₋ | √ | √ | ₋ |
|  | 49-280 | √ | √ | ₋ | √ | √ | √ |
|  | 49-281 | √ | √ | ₋ | √ | √ | √ |
| Price Industries www.priceindustries.com | LBP/LBPH 15B | √ | √ | ₋ | √ | √ | √ |
|  | LBP/LBPH 16B | √ | √ | ₋ | √ | √ | √ |
|  | LBP/LBPH 25C | ₋ | ₋ | ₋ | √ | ₋ | ₋ |
| NOTE: Vanes or deflectors options with grille are prohibited. |  |  |  |  |  |  |  |

Figure 3

Standard Watt Density Models 250W/ft.

| Watts | Watts 240/208V | # Product |  |  |  |  |  |  |  |  |  |  |  | Length |  | Weigth |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 120V | Qty | 208V | Qty | 240/208V | Qty | 277V | Qty | 347V | Qty | 600V | Qty | In | mm | lb | kg |
| 750 | 750/563 | OTS0752 |  | OTS0758 |  | OTS0750 |  | OTS0777 |  | - | - | - | - | 36 | 915 | 8.4 | 3.8 |
| 1000 | 1000/750 | - | - | OTS1008 |  | OTS1000 |  | OTS1077 |  | OTS1007 |  | OTS1006 |  | 48 | 1220 | 10.8 | 4.9 |
| 1250 | 1250/938 | - | - | OTS1258 |  | OTS1250 |  | OTS1277 |  | OTS1257 |  | OTS1256 |  | 60 | 1525 | 13.2 | 6.0 |

- Low Watt Density Models

| Product # 1 | Length | Weight | Average Density W/ft. | Watts | Watts 240/208V | 120V | Qty | 208V | Qty | 240/208V | Qty | 347V | Qty | 600V | Qty |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| OTS050X-915 | 36’’ (915 mm) | 8.4 lb (3.8 kg) | 167 | 500 | 500/375 |  |  |  |  |  |  | ----- | ----- | ----- | ----- |
| OTS060X-915 |  |  | 200 | 600 | 600/450 |  |  |  |  |  |  | ----- | ----- | ----- | ----- |
| OTS066X-1220 | 48’’ (1220 mm) | 10.8 lb (4.9 kg) | 167 | 668 | 668/502 |  |  |  |  |  |  |  |  |  |  |
| OTS080X-1220 |  |  | 200 | 800 | 800/600 |  |  |  |  |  |  |  |  |  |  |
| OTS083X-1525 | 60’’ (1525 mm) | 13.2 lb (6 kg) | 167 | 835 | 835/627 |  |  |  |  |  |  |  |  |  |  |
| OTS100X-1525 |  |  | 200 | 1000 | 1000/750 | ----- | ----- |  |  |  |  |  |  |  |  |

1 X = 2 (120V), 8 (208V), 0 (240/208V), 7 (347V), 6 (600V).

-  = Available.

Add "NL" for semi-gloss black. Upcharge applicable for optional colors shown in the color chart section.

Other voltages available upon request.

Options

| Product # 1 Kit | Product # 1 Factory installed* | Description | Qty |
| --- | --- | --- | --- |
| KIT-OTS-DIS20 | DIS20 | Disconnect switch, 20A at 277V max. |  |
| KIT-OTS-DIS40 | - | Disconnect switch, 40A at 600V max. 120 mm height |  |
| KIT-OTS-R-347 | R | Single-pole relay, coil 24V, without transformer: 22A at 120V, 208V, 240V - 19A at 277V - 18A at 347V |  |
| KIT-OTS-R-600 | R | Single-pole relay, coil 24V, without transformer: 10A at 480V, 600V |  |
| KIT-OTS-RT-208 | RT | Single-pole relay, coil 24V, with transformer 208V/24V, 22A at 208V |  |
| KIT-OTS-RT-240 | RT | Single-pole relay, coil 24V, with transformer 240V/24V, 22A at 240V |  |
| KIT-OTS-RT-277 | RT | Single-pole relay, coil 24V, with transformer 277V/24V, 19A at 277V |  |
| KIT-OTS-RT-347 | RT | Single-pole relay, coil 24V, with transformer 347V/24V, 18A at 347V |  |
| KIT-OTS-TRIAC-347 | TRIAC | Single-pole electronic relay, coil 24V, without transformer: 10A max. at 347V max. |  |
| KIT-OTS-TRIAC-347T | TRIACT | Single-pole electronic relay, coil 24V, with transformer: 10A max. at 347V max. |  |
| KIT-OTS-TRIAC-600 | TRIAC | Single-pole electronic relay, coil 24V, without transformer: 6A at 600V max. |  |

* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover.

1 Options installed at right end only.

### Others

| Type | Quantity | Model et description Complementary information | Volts | Phase | Watts | Length mm/in. | Information Color/installation |
| --- | --- | --- | --- | --- | --- | --- | --- |

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrician Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact in Ouellet: |  |
| Comments: |  |