- Series

OWD	Wash Down Unit Heater

- Features

Voltage	-	208V, 240V, 277V, 480V, 600V, 1 or 3-phase.

Construction	-	16-gauge, 304 stainless steel, moisture and corrosion resistant housing*.

-	Adjustable, stainless steel outlet louvers.

-	Stainless steel rear grille to protect against accidental contact with the fan blade.

-	High-limit temperature control with automatic reset 
(manual reset available upon request).

-	NEMA 4X non-metallic electrical enclosure.

-	Pilot light (power-on indicator) available.

-	Optional disconnect switch with lockable handle available.

Fan	-	Anodized aluminum, delayed-action fan.

-	Enclosed epoxy coated motor with permanently lubricated ball bearing for longer life.

-	Epoxy-painted fan.

-	Designed to resist moisture and corrosion.

Heating element	-	Sealed tubular heating element with 316* stainless steel fins.

Control	-	24V control circuit with transformer and contactor.

-	Built-in capillary thermostat available.

-	Fan switch control available.

Installation	-	Electrical enclosure located at bottom of unit for ease of installation and servicing.

-	Stainless steel swivel mounting bracket included, for wall or ceiling mounting.

Warranty	-	1-year warranty against defects.

Application	-	Food industry, marine and offshore, car wash, dairy.

*Caution: Some environments can be corrosive for this type of stainless steel. Please check the application prior to installation.

- Models

| kW | BTU/hr | Product # |  |  |  |  |  |  |  |  |  |  |  | cfm | Temperature Rise |  | Air Throw |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 208V (1 ph) | Qty | 208V (3 ph) | Qty | 240V (1 ph) | Qty | 240V (3 ph) | Qty | 480V (3 ph) | Qty | 600V (3 ph) | Qty |  | oC | oF | ft. | m |
| 3.0 | 10236 | OWD03008 |  | OWD03038 |  | OWD03000 |  | OWD03030 |  | OWD03034 |  | OWD03036 |  | 700 | 8 | 14 | 26 | 8 |
| 5.0 | 17060 | OWD05008 |  | OWD05038 |  | OWD05000 |  | OWD05030 |  | OWD05034 |  | OWD05036 |  | 700 | 13 | 24 | 26 | 8 |
| 7.5 | 25590 | OWD07508 |  | OWD07538 |  | OWD07500 |  | OWD07530 |  | OWD07534 |  | OWD07536 |  | 700 | 19 | 35 | 26 | 8 |
| 9.0 | 30708 | OWD09008 |  | OWD09038 |  | OWD09000 |  | OWD09030 |  | OWD09034 |  | OWD09036 |  | 1450 | 11 | 20 | 43 | 13 |
| 10.0 | 34120 | - | - | OWD10038 |  | OWD10000 |  | OWD10030 |  | OWD10034 |  | OWD10036 |  | 1450 | 12 | 22 | 43 | 13 |
| 12.0 | 40944 | - | - | OWD12038 |  | - | - | OWD12030 |  | OWD12034 |  | OWD12036 |  | 1450 | 14 | 26 | 43 | 13 |
| 12.5 | 42650 | - | - | OWD12538 |  | - | - | OWD12530 |  | OWD12534 |  | OWD12536 |  | 2400 | 9 | 17 | 50 | 15 |
| 15.0 | 51180 | - | - | OWD15038 | - | - | - | OWD15030 |  | OWD15034 |  | OWD15036 |  | 2400 | 12 | 21 | 50 | 15 |
| 20.0 | 68240 | - | - | - | - | - | - | - |  | OWD20034 | - | OWD20036 |  | 2400 | 16 | 28 | 50 | 15 |
| 25.0 | 85300 | - | - | - | - | - | - | - |  | OWD25034 | - | OWD25036 |  | 2400 | 19 | 35 | 50 | 15 |
| 30.0 | 102360 | - | - | - | - | - | - | - |  | OWD30034 | - | OWD30036 |  | 2400 | 23 | 42 | 50 | 15 |
| 35.0 | 119420 | - | - | - | - | - | - | - |  | OWD35034 | - | OWD35036 |  | 2400 | 27 | 48 | 50 | 15 |
| 38.4 | 131020 | - | - | - | - | - | - | - |  | OWD38434 | - | OWD38436 |  | 2400 | 30 | 54 | 50 | 15 |
| 47.0 | 160364 | - | - | - | - | - | - | - |  | - | - | OWD47036 |  | 2400 | 36 | 64 | 50 | 15 |

277V available upon request.

Options

| # Product # # Kit | # Product # # Factory Installed* | Description | Qty |
| --- | --- | --- | --- |
| - | 120 | 120V control circuit |  |
| - | EP | Epoxy paint finish for better corrosion resistance in certain environments |  |
| - | I1 | Disconnect switch with lockable handle available |  |
| - | L | Pilot light "power-on indicator" |  |
| - | ME1 | Monel elements, for 3 to 20kW units for better corrosion resistance in certain environments |  |
| - | ME2 | Monel elements, for 25 to 38.4kW units for better corrosion resistance in certain environments |  |
| - | PTM | High-limit temperature control with manual reset |  |
| - | S | Three-position switch: On/Standby/Fan |  |
| - | T | Thermostat |  |
| - | T2S | 2-stage thermostat |  |
| OWD-TM | - | NEMA 4X wall thermostat, range 4 °C to 43 °C (40 °F to 110 °F): 25A at 120V, 208V, 240V – 22A at 277V (Compatible avec circuit de contrôle à 24VAC) |  |

* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover.

1 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect.

277V available upon request.

### Others

| Type | Quantity | Model et description Complementary informations | Volts | Phase | Watts | Length mm/in. | Informations Color/installation |
| --- | --- | --- | --- | --- | --- | --- | --- |

- Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrician Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact in Ouellet: |  |
| Comments: |  |