# Series

AHX	Atex/IECEx Approved Explosion-Proof Unit Heater

# Features

Color	-	Standard: red.

Finish	-	Standard: epoxy/polyester powder paint.

Voltage	-	400V, 50 Hz only, 3-phase.

- 480V, 60 Hz only, 3-phase.

Construction	-	2 mm (14-gauge) steel cabinet.

- Adjustable anodized extruded aluminum louvers.

-	Flameproof (Ex d) cast aluminum with O-ring.

- Split design protection grille with close wire spacing. A 9.5 mm diameter 
probe will not enter.

- Black polyester powder coated protection grille.

Protection	-	High temperature pressure relief device.

- Two high-limit temperature controls:

one with automatic reset and one with manual reset.

- Thermal delay fuse.

Fan	-	Flameproof (Ex d) thermally protected, 1500 rpm (nominal) permanently lubricated 
ball bearing type with 71 frame and “easyoff” fan blade replacement feature.

-	0.37Kw (½ HP).

Heat exhanger	-	High grade metal-sheathed elements ﬁns with ethylene glycol and water including 
corrosion inhibitors.

-	Carbon steel shells and carbon steel tubes with copper-free, roll-formed aluminum 
fins @ 2.5 mm pitch.

Hazardous location approvals	-	ATEX (Gas Atmospheres)

SIRA 13 ATEX 1240X

0518  II 2G Ex d IIB T4 Gb IP55

-40 oC ≤ Tamb ≤ +40 oC (Suitable for Zone 1 and 2)

-	IECEx (Gas Atmospheres)

IECEX CSA 13.0034X

Ex d IIB T4 Gb IP55, -40 oC ≤ Tamb ≤ +40 oC (Suitable for Zone 1 and 2)

Control	-  24V control.

-	Optional wall mounted thermostat.

Installation			        -  Accessories available.

Warranty	-	3-year warranty against defects.

Application	-	Paint room, petrochemical plant, reﬁnery, chemical plant, mining industry, aircraft servicing areas, oil & gas drilling, sewage treatment plant.

Consult the Electrical Code in your area before installing this unit.

# Models

| kW | BTU/hr | Product # | To Rise (oC) | Weight1 |
| --- | --- | --- | --- | --- |
|  |  | 400V 50 Hz (3 ph) | Qty | 480V 60 Hz (3 ph) | Qty | 50 Hz | 60 Hz | lb | kg |
| 5.0 | 17060 | AHX0503950 |  | AHX0503460 |  | 21.2 | 17.7 | 144 | 65.4 |
| 7.5 | 25590 | AHX0753950 |  | AHX0753460 |  | 22.4 | 18.7 | 144 | 65.4 |
| 10.0 | 34120 | AHX1003950 |  | AHX1003460 |  | 21.6 | 18.0 | 148 | 67.2 |
| 15.0 | 51180 | AHX1503950 |  | AHX1503460 |  | 21.7 | 18.1 | 176 | 79.8 |
| 20.0 | 68240 | AHX2003950 |  | AHX2003460 |  | 20.7 | 17.3 | 176 | 79.8 |
| 25.0 | 85300 | AHX2503950 |  | AHX2503460 |  | 20.8 | 17.4 | 201 | 91.5 |
| 30.0 | 102360 | AHX3003950 |  | AHX3003460 |  | 17.5 | 14.6 | 201 | 91.5 |

Options

| Product # | Description | Factory Installed | Kit | Qty |
| --- | --- | --- | --- | --- |
| AHX-MB1 | Basic mounting bracket, 5 to 10kW units | - | ( |  |
| AHX-MB2 | Basic mounting bracket, 15 to 20kW units | - | ( |  |
| AHX-MB3 | Basic mounting bracket, 25 to 30kW units | - | ( |  |
| AHX-MM1 | Wall mounting bracket, 5 to 10kW units | - | ( |  |
| AHX-MM2 | Wall mounting bracket, 15 to 20kW units | - | ( |  |
| AHX-MM3 | Wall mounting bracket, 25 to 30kW units | - | ( |  |
| AHX-MS | Hanging mounting bracket, all models | - | ( |  |
| AHX-MT1 | Pipe mounting bracket, 5 to 10kW units | - | ( |  |
| AHX-MT2 | Pipe mounting bracket, 15 to 20kW units | - | ( |  |
| AHX-MT3 | Pipe mounting bracket, 25 to 30kW units | - | ( |  |
| B121-13272 | Explosion-proof wall thermostat range of -9.4 °C to 60 °C (15 °F to 140 °F) | - | ( |  |

1 Shipping weight.

Standard color is red.

# Approved locations

- ATEX (Gas Atmospheres)

SIRA 13 ATEX 1240X

0518  II 2G Ex d IIB T4 Gb IP55

-40 oC ≤ Tamb ≤ +40 oC (Suitable for Zone 1 and 2)

-	IECEx (Gas Atmospheres)

IECEX CSA 13.0034X

Ex d IIB T4 Gb IP55

-40 oC ≤ Tamb ≤ +40 oC (Suitable for Zone 1 and 2)

# Temperature limitations

Ambient temperature: -40 °C to +40 °C

Storage temperature: -40 °C to +60 °C

Maximum altitude: 3000 m above sea level.

### Others

| Type | Quantity | Model et description Complementary informations | Volts | Phase | Watts | Length mm/in. | Informations Color/installation |
| --- | --- | --- | --- | --- | --- | --- | --- |

# Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Eectrician Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact in Ouellet: |  |
| Comments: |