Series

SLIM24 Hyper Heat

Central Heat Pump System and Cased Coil System

Features

Operation mode	- 	Cooling, heating, dehumidifying, fan and auto.

Nominal capacity	-		24000, 36000, 48000, 60000 BTU/hr.

Voltage	-	230/208V, 60 Hz, 1-phase.

Indoor unit	Air Handler

- 	Vertical or horizontal installation.

-	Available with upflow or downflow.

-	Washable filters.

Cased Coil

- Available in four casing dimensions.

- Horizontal or vertical installation.

- Can be matched with third-party gas furnace or blower.

- 24V or 485 communication mode.

Outdoor unit	-	DC motor.

-	Variable speed rotary compressor (INVERTER), with overload protection.

-	Electronic expansion valve for precise control of refrigerant flow.

-	Condenser fins covered with a hydrophilic coating for improved corrosion resistance.

-	Large diameter quiet axial-flow fan for more efficient heat exchange.

-	Multi-hole pan with smart heater to prevent ice formation.

-	Compressor blanket and preheating technology.

-	Installation on aluminum wall bracket or ground stand (optional).

Connection piping	-	Minimum piping length of 10 ft. (3 m).

- Flared connections.

Control 	-	Wireless remote included.

-	Wi-Fi wired wall controller included.

- 	24V thermostat connection available.

-	Set temperature: 16 to 30 °C (61 to 86 °F).

-	Temperature display format: °C or °F.

Warranty	- 10-year basic warranty on parts and 10-year basic warranty on the compressor (labour not included).

- Labour warranty (sold separately) from the 1st to 10th year, on parts and labour with system replacement if the compressor fails.

Application	-	Detached and semi-detached home, commercial building, office building, restaurant.

Features and functions

Models

| Product #1 |  | Indoor Unit |  |  | DEV24H2R19 SHV24H2R20 | DEV36H2R19 SHV36H2R20 |  | DEV48H2R19 SHV48H2R20 |  |  | DEV60H2R19 SHV60H2R20 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Outdoor Unit |  |  |  |  |  |  |  |  |  |
| Qty |  |  |  |  |  |  |  |  |  |  |  |
| Technical Performance |  |  |  |  |  |  |  |  |  |  |  |
| Power supply |  |  |  | V / Ph / Hz | 230/208 / 1 / 60 |  |  |  |  |  |  |
| Cooling capacity | Nominal |  |  | W (BTU/hr) | 7038 (24000) | 10557 (36000) |  | 13783 (47000) |  |  | 16129 (55000) |
|  | Min. – max. |  |  | W (BTU/hr) | 3225 - 7918 (11000 - 27000) | 3519 - 13900 (12000 - 47400) |  | 5279 - 14076 (18000 - 48000) |  |  | 4106 - 16422 (14000 - 56000) |
| Heating capacity | Nominal |  |  | W (BTU/hr) | 7038 (24000) | 11730 (40000) |  | 14663 (50000) |  |  | 17302 (59000) |
|  | Min. – max. |  |  | W (BTU/hr) | 2962 – 9091 (10100 - 31000) | 3226 - 16774 (11000 - 57200) |  | 3226 - 16129 (11000 - 55000) |  |  | 3930 - 20235 (13400 - 69000) |
| SEER / SEER2 |  |  |  | - | 20 / 17.4 | 18 / 16 |  | 16 / 15.6 |  |  | 16.4 / 15.3 |
| HSPF / HSPF2 |  |  |  | - | 12 / 10 | 10.5 / 9.5 |  | 10 / 9.4 |  |  | 10.5 / 9.4 |
| EER |  |  |  | W/W | 13 | 10.5 |  | 8.5 |  |  | 9 |
| COP |  |  |  | W/W | 3 | 1.8 |  | 1.88 |  |  | 1.92 |
| AHRI number |  |  |  | - | 210343158 | 210343156 |  | 210343157 |  |  | 210343159 |
| Indoor Unit (Air Handler) |  |  |  |  |  |  |  |  |  |  |  |
| Dehumidification |  |  | pt/hr (l/hr) |  | 3.48 (1.98) | 6.1 (3.49) |  | 4.96 (8.72) |  |  | 9.77 (5.55) |
| Air flow volume | T / H / M / L2 |  | cfm |  | 824 / 759 / 694 / 629 | 1188 / 1082 / 971 / 865 |  | 1471 / 1282 / 1094 / 906 |  |  | 1806 / 1582 / 1359 / 1135 |
| Sound level | H / M / L2 |  | dB (A) |  | 39 / 36 / 33 | 45 / 43 / 41 |  | 50 / 47 / 43.5 |  |  | 51 / 45.5 / 41.5 |
| Fan motor RLA |  |  | A |  | 3 | 4 |  | 6 |  |  | 7 |
| MCOP |  |  | A |  | 15 | 15 |  | 15 |  |  | 15 |
| External Static Pressure (ESP) | Nominal |  | inH2O |  | 0.1 | 0.15 |  | 0.2 |  |  | 0.2 |
|  | Range |  | inH2O |  | 0 - 0.8 | 0 - 0.8 |  | 0 - 0.8 |  |  | 0 - 0.8 |
| Net weight |  |  | lb (kg) |  | 106 (48) | 129 (59) |  | 131 (59) |  |  | 163 (74) |
| Outdoor Unit |  |  |  |  |  |  |  |  |  |  |  |
| Air flow volume |  |  | cfm |  | 3000 | 4500 |  | 4412 |  |  | 4500 |
| Sound level |  |  | dB (A) |  | 64 | 64 |  | 64 |  |  | 64 |
| Compressor power input |  |  | W |  | 1945 | 3565 |  | 3565 |  |  | 3770 |
| MCA |  |  | A |  | 20.5 | 41 |  | 42 |  |  | 42 |
| MCOP |  |  | A |  | 35 | 50 |  | 50 |  |  | 60 |
| Compressor RLA |  |  | A |  | 15 | 32 |  | 33 |  |  | 26.2 |
| Fan motor power output |  |  | W |  | 120 | 85 |  | 85 |  |  | 85 |
| Fan motor RLA |  |  | A |  | 1.35 | 1.2 |  | 1.2 |  |  | 1.2 |
| Refrigerant volume (R410A) |  |  | oz (g) |  | 102 (2900) | 165.7 (4700) |  | 169 (4800) |  |  | 169 (4800) |
| Operating ambient temperature | Cooling |  | °C (°F) |  | -15 to 50 (5 to 112) |  |  |  |  |  |  |
|  | Heating |  | °C (°F) |  | -30 to 24 (-22 to 75) |  |  |  |  |  |  |
| Net weight |  |  | lb (kg) |  | 137 (62) |  | 227 (103) |  | 220 (100) | 240 (108) |  |
| Connection Piping / Refrigerant |  |  |  |  |  |  |  |  |  |  |  |
| Pre-charge length |  |  | ft. (m) |  | 25 (7.5) | 25 (7.5) |  | 25 (7.5) |  |  | 25 (7.5) |
| Additional refrigerant charge |  |  | oz/ft. (g/m) |  | 0.69 (65) | 0.69 (65) |  | 0.69 (65) |  |  | 0.69 (65) |
| Liquid pipe outer diameter |  |  | in. |  | 3/8 | 3/8 |  | 3/8 |  |  | 3/8 |
| Gas pipe outer diameter |  |  | in. |  | 3/4 | 3/4 |  | 3/4 |  |  | 7/8 |
| Maximum height between outdoor and indoor units |  |  | ft. in. (m) |  | 82’ (25) | 98’ 5’’ (30) |  | 98’ 5’’ (30) |  |  | 98’ 5’’ (30) |
| Maximum pipe length between outdoor and indoor units |  |  | ft. in. (m) |  | 164’ (50) | 213’ 3’’ (65) |  | 213’ 3’’ (65) |  |  | 213’ 3’’ (65) |

1 1 indoor unit and 1 outdoor unit. Note that each unit is individually packaged.

2 Fan Speeds: (T) Turbo / (H) High / (M) Medium / (L) Low.

Models – Indoor Unit (Cased Coil)

| Product # |  |  | Indoor Unit | MAC24H1718E | MAC36H1724E | MAC36H2124E | MAC48H2124E | MAC60H2428E |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Outdoor Unit | SHV24H2R20 | SHV36H2R20 | SHV36H2R20 | SHV48H2R20 | SHV60H2R20 |
| Qty |  |  |  |  |  |  |  |  |
| Power supply |  | V / Ph / Hz |  | 208/230 / 1 / 60 |  |  |  |  |
| Capacity | Cooling | BTU/hr |  | 24000 | 35000 | 36000 | 46000 | 53000 |
|  | Heating | BTU/hr |  | 25000 | 38000 | 39000 | 51000 | 54000 |
| AHRI number |  | - |  | 213160473 | 213160474 | 213160476 | 213160477 | 213160478 |
| Heating at -15 °C (5 °F) |  | SEER2 |  | 16.8 | 15.5 | 14.8 | 14.3 | 14.5 |
|  |  | EER2 BTU/W |  | 10.7 | 10 | 9.8 | 8.6 | 8.6 |
|  |  | HSPF2 |  | 9.5 | 8.6 | 8 | 9 | 8.6 |
|  |  | Maximum BTU/hr |  | 20000 | 31600 | 32000 | 40000 | 46500 |
|  |  | COP W/W |  | 1.95 | 1.85 | 2 | 1.8 | 1.8 |
| Refrigerant piping | Liquid – Gas | in. |  | 3/8 - 3/4 | 3/8 - 3/4 | 3/8 - 3/4 | 3/8 - 3/4 | 3/8 - 7/8 |
| Drain pipe diameter |  | in. |  | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 |
| Dimension | W x D x H | in. |  | 17 ½ x 21 x 18 | 17 ½ x 21 x 23 ½ | 21 x 21 x 24 | 21 x 21 x 24 | 24 ½ x 21 x 28 |
|  | W x D x H | mm |  | 445 x 533 x 457 | 445 x 533 x 599 | 533 x 533 x 609 | 533 x 533 x 609 | 622 x 533 x 711 |
| Net weight |  | lb (kg) |  | 43 (19) | 60 (27) | 67 (30) | 67 (30) | 87 (39) |

| Indoor Unit Air Handler | A |  | B |  |  | C |  | D |  | E |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | po | mm | po |  | mm | po | mm | po | mm | po | mm |
| DEV24H2R19 | 45 | 1143 | 21 |  | 534 | 17 1/2 | 445 | 15 3/4 | 400 | 10 1/4 | 260 |
| DEV36H2R19 | 49 | 1245 | 21 |  | 534 | 21 | 534 | 19 1/4 | 490 | 10 1/4 | 260 |
| DEV48H2R19 | 49 | 1245 | 21 |  | 534 | 21 | 534 | 19 1/4 | 490 | 10 1/4 | 260 |
| DEV60H2R19 | 53 | 1346 | 21 |  | 534 | 24 1/2 | 622 | 22 7/8 | 580 | 10 1/4 | 260 |
| Indoor Unit Cased Coil | W |  | D |  |  |  |  | H |  |  |  |
|  | po | mm | po |  |  | mm |  | po |  | mm |  |
| MAC24H1718E | 17 1/2 | 445 | 21 |  |  | 533 |  | 18 |  | 457 |  |
| MAC36H1724E | 17 1/2 | 445 | 21 |  |  | 533 |  | 23 1/2 |  | 599 |  |
| MAC36H2124E | 21 | 533 | 21 |  |  | 533 |  | 24 |  | 609 |  |
| MAC48H2124E | 21 | 533 | 21 |  |  | 533 |  | 24 |  | 609 |  |
| MAC60H2428E | 24 1/2 | 622 | 21 |  |  | 533 |  | 28 |  | 711 |  |
| Outdoor Unit | W |  | H |  |  | D |  | A |  | B |  |
|  | po | mm | po | mm |  | po | mm | po | mm | po | mm |
| SHV24H2R20 | 40 1/2 | 1030 | 32 | 810 |  | 17 7/8 | 455 | 26 1/2 | 673 | 15 7/8 | 404 |
| SHV36H2R20 | 41 1/4 | 1045 | 52 1/2 | 1333 |  | 18 | 457 | 25 | 634 | 15 7/8 | 404 |
| SHV48H2R20 | 41 1/4 | 1045 | 52 1/2 | 1333 |  | 18 | 457 | 25 | 634 | 15 7/8 | 404 |
| SHV60H2R20 | 41 1/4 | 1045 | 52 1/2 | 1333 |  | 18 | 457 | 25 | 634 | 15 7/8 | 404 |

Compatibility table for electrical heating elements

| Electric heater power | 24K BTU | 36K BTU | 48K BTU | 60K BTU |
| --- | --- | --- | --- | --- |
| 5kW | X | X | - | - |
| 8kW | X | X | X | - |
| 10kW | X | X | X | X |
| 15kW | X | X | X | X |
| 20kW | - | X | X | X |
| 25kW | - | - | - | X |

Options

| # Produit Kit | Description | Qty |
| --- | --- | --- |
| Electric auxiliary heat module (for Air Handler only) |  |  |
| OTP-EAH-05B-UL | 5kW electric auxiliary heat module |  |
| OTP-EAH-10B-UL | 10KW electric auxiliary heat module |  |
| OTP-EAH-15B-UL | 15kW electric auxiliary heat module |  |
| OTP-EAH-20B-UL | 20kW electric auxiliary heat module |  |
| QOU14100JBAF | 4 poles jumper bar assy |  |

Specifications may change without prior notice

| Project: | Approval Information |
| --- | --- |
| Consultant Engineer: |  |
| Electrical Contractor: |  |
| Distributor: |  |
| Date: |  |
| Contact at manufacturer: |  |
| Comments: |  |